## Cover Page
Aylestone Business and Enterprise College
Summary Report
Contents
|  | Section | Page | No. of pages
Aylestone Business and Enterprise College |  | Summary Data | 3 | 1
|  | General Information and Asset Summary | 4 | 1
Summary Report |  | Maintenance and Condition Summary | 5 | 2
|  | Education Funding Agency Condition Survey Data | 7 | 1
Schools Capital Investment Strategy |  | Suitability and Compliance Summary | 8 | 2
|  | School Occupancy Summary | 10 | 1
|  | School Statistics | 11 | 1
|  | Environmental Sustainability Condition | 12 | 1
|  | Parental Preference | 13 | 1
|  | Distribution of Children Attending School or Resident in its Catchmnet Area | 14 | 2
|  | Distribution of Children Attending School or Where it is the Nearest School | 16 | 2
|  | Key Services Within 2 Mile Radius of School | 18 | 1
|  | Key Services Adjacent to School | 19 | 1
|  | Disability Access | 20 | 1
Children's Wellbeing
Herefordshire Council
Plough Lane Offices
Plough Lane
HEREFORD
HR4 0LE

## Summary Info
Aylestone Business and Enterprise College
Summary Report
Summary of Headline Information
Asset Summary | [5 empty] | Occupancy Summary
Gross Site Area (M2)(whole site including building):- |  | 62062 |  |  |  | Current Capacity (incl post 16):- |  |  | 450
Insurance Asset Value (£000):- |  | 14458891 |  |  |  | Current Capacity (excl post 16):- |  |  | 450
Land Asset Value (£000):- |  | Not Known |  |  |  | Current Planned Admission No.:- |  |  | 90
Land Ownership:- | Owned by the Local Authority |  |  |  |  | Current Occupancy (incl post 16):- |  |  | 441
[6 empty] | Current Occupancy (excl post 16):- |  |  | 441
[6 empty] | Current Total Number Over Capacity:- |  |  | 0
[6 empty] | Current Total Number Under Capacity:- |  |  | 9
Maintenance Expenditure Required on the School over a 5 Year Period Summary
Survey Date:- |  |  |  | 2012-09-01
Backlog Maintenance Total (£000):- | [6 empty] | 557.7361
Total Forecast Expenditure (5 years) (£000):- | [6 empty] | 329.9857
Total Potential Local Authority Forecast Expenditure (£000):- | [6 empty] | 642.4885
Total Potential School Forecast Expenditure (£000):- | [6 empty] | 111.893
Suitability and Compliance
Compliance Percentage of Recommended Basic Teaching Spaces:- | [6 empty] | 154.4484 | Required Building Footprint (M2):- | 4175.55
Compliance Percentage of Recommended Hall Size:- | [6 empty] | 112.5845 | Current Building Area (M2):- | 6575.772
Compliance Percentage of Recommended Storage Space:- | [6 empty] | 338.2183 | Area Shortfall (M2):- | 0
Compliance Percentage of Recommended Staff and Admin Space:- | [6 empty] | 262.8325 | Area Surplus (M2):- | 2400.222
Compliance Percentage of Recommended Learning Resource Space:- | [6 empty] | 154.1 | Total Percentage Compliance:- | 157.4828
Number of Temporary Buildings on Site:- | [6 empty] | 3 | Required Net Site Area (M2):- | 31190.7
Number of Classrooms in Temporary Buildings:- | [6 empty] | 1 | Current Net Site Area (M2):- | 55486.228
Compliance Percentage of Recommended Pupil Toilets:- | [6 empty] | 154.1667 | Area Shortfall (M2):- | 0
[8 empty] | Area Surplus (M2):- | 24295.528
[8 empty] | Total Percentage Compliance:- | 177.8935
Disability Access
Rating:- | 1 |  | Details:- |  |  |  | Partly accessible
Environmental Sustainability Condition
DEC Rating:- |  |  |  |  | C
Electric Consumption 2014/Child:- |  |  |  |  | 599.0167
Gas Consumption 2014/Child:- |  |  |  |  | 1475.7238
School Statistics
Ofsted Results:- | [8 empty] | Good
Percentage of Children Achieving KS4 5+ A*-C GCSEs (or equivalent) including English and maths GCSEs in 2014:- | [8 empty] | 50
Parental Preference (2014)
Percentage of Parental First Preference Applications:- | [6 empty] | 48.6667
Total Number of Children within Catchment:- | [6 empty] | 1063
Total Number of Children at School from Catchment:- | [6 empty] | 347
Percentage of Catchment at School:- | [6 empty] | 72.5941
Percentage of Catchment Going to School:- | [6 empty] | 32.6435

## Report
|  |  |  | Aylestone Business and Enterprise College | [6 empty] | Aylestone Business and Enterprise College | [14 empty] | Aylestone Business and Enterprise College | [7 empty] | Aylestone Business and Enterprise College |  |  |  |  | Aylestone Business and Enterprise College |  | Aylestone Business and Enterprise College | [12 empty] | Aylestone Business and Enterprise College | [5 empty] | Aylestone Business and Enterprise College |  |  | Aylestone Business and Enterprise College | [8 empty] | Aylestone Business and Enterprise College |  | Aylestone Business and Enterprise College |  | Aylestone Business and Enterprise College |  | Aylestone Business and Enterprise College |  | Aylestone Business and Enterprise College |  | Aylestone Business and Enterprise College |  | Aylestone Business and Enterprise College |  |  | Aylestone Business and Enterprise College
|  |  |  | Summary Report | [6 empty] | Summary Report | [14 empty] | Summary Report | [7 empty] | Summary Report |  |  |  |  | Summary Report |  | Summary Report | [12 empty] | Summary Report | [5 empty] | Summary Report |  |  | Summary Report | [8 empty] | Summary Report |  | Summary Report |  | Summary Report |  | Summary Report |  | Summary Report |  | Summary Report |  | Summary Report |  |  | Summary Report
General Information |  |  |  |  | Maintenance and Condition Summary | [21 empty] | Education Funding Agency Condition Survey Data | [7 empty] | Suitability and Compliance Summary |  |  |  |  | Suitability and Compliance Summary (continued) |  | School Occupancy Summary | [12 empty] | School Statistics | [5 empty] | Environmental Sustainability Condition |  |  | Parental Preference | [8 empty] | Distribution of Children Attending School or Resident in its Catchment Area |  | Distribution of Children Attending School or Resident in its Catchment Area (continued) |  | Distribution of Children Attending School or Where it is the Nearest School |  | Distribution of Children Attending School or Where it is the Nearest School (continued) |  | Key Services Within 2 Mile Radius of School |  | Key Services Adjacent to School |  | Disability Access
Maintenance and Condition Summary (continued)
School Name:- | Aylestone Business and Enterprise College |  |  |  | Survey Date:- | 2012-09-01 |  | Survey Company:- |  | Amey |  | Key Elements and Annual Forecast Maintenance Costs and Responsibilities | [14 empty] | Date of Survey:- |  | 2013-06-10 | [5 empty] | Areas | Standard Criteria (M2) (PAN 90) | Schools Compliance (M2) | Compliance Percentage |  |  |  | Current Planned Admission No. (PAN) | Post 16 Planned Admission No. (PAN) |  |  | Current School Capacity |  |  | Maximum PAN |  |  | Maximum Capacity Based on PAN |  |  | Year | KS4 Year on Year Results |  |  |  |  | Electric Consumption 2014/Child:- | 599.0167 |  |  | Parental First Preference Applications | [19 empty] | Physical Accessibility Rating
Head Teacher:- | Mr S Robertson |  | DFE Number:- | 4015 | Year | Forecast Maintenance Costs (£ 000) | [5 empty] | Year | External Grounds |  | Roof Works |  | External Walls |  | Windows and Doors |  | Internal Works |  | Mechanical & Electrical |  | Other |  | Number of Occurences Identified Within the Report | [7 empty] | Basic Teaching Space | 1473.75 | 2276.183 | 154.4484 |  |  |  | 90 | - |  |  | 450 |  |  | 111.6 |  |  | 558 |  |  |  | School - Percentage achieving 5+ A*-C GCSEs (or equivalent) including English and maths GCSEs | LA - Percentage achieving 5+ A*-C GCSEs (or equivalent) including English and maths GCSEs | All Schools in England - Percentage achieving 5+ A*-C GCSEs (or equivalent) including English and maths GCSEs |  |  | Gas Consumption 2014/Child:- | 1475.7238 |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | [14 empty] | Rating: | 1
Leadership:- | Federated with Withington and Broadlands Primary Schools | [25 empty] | Rating (see key below) | External Grounds | Roof Works | External Walls | Windows and Doors | Internal Works | Mechanical & Electrical | Other | Hall and Studio | 742.5 | 835.94 | 112.5845 | [25 empty] | PAN | 210 | 180 | 150 | 150 | 150 | 150
Address:- | Aylestone Business and Enterprise College, Broadlands House, Broadlands Lane, Hereford HR1 1HY |  | Email:- | admin@aylestone.hereford.sch.uk | Backlog | 557.7361 | [5 empty] | £ 000 | School | LA | School | LA | School | LA | School | LA | School | LA | School | LA | School | LA | [8 empty] | Storage | 308.75 | 1044.249 | 338.2183 |  |  |  | Historical Numbers on Roll Data (Spring Census) | [21 empty] | Number | 115.5 | 86.4 | 96 | 103.05 | 87 | 73 | [14 empty] | Details: | Partly accessible
[5 empty] | 2015 | 63.305 |  |  | 557.7361 |  |  | Backlog | 1.5558 | 0 | 8.9662 | 348.4943 | 3.4574 | 2.3049 | 3.1808 | 95.77 | 2.328 | 5.1861 | 32.0962 | 54.3964 | 0 | 0 | C1 |  |  |  | 1 |  |  |  | Staff and Admin | 261.25 | 686.65 | 262.8325 |  |  |  | Year | NOR |  |  | Capacity Based on PAN |  |  | Shortfall |  |  | Surplus |  |  | 2011 | 58 | 57.5 | 59 | [5 empty] | Percentage | 55 | 48 | 64 | 68.7 | 58 | 48.6667
[5 empty] | 2016 | 58.891 |  |  | 63.305 |  |  | 2015 | 0.32269 | 0 | 1.383 | 0 | 2.5354 | 0 | 0 | 0 | 0 | 0 | 16.8836 | 42.1803 | 0 | 0 | C2 | 1 | 4 | 5 | 5 | 7 | 4 |  | Learning Resource | 190 | 292.79 | 154.1 |  |  |  |  | 11-16 | Post 16 | Total | 11-16 | Post 16 | Total | 11-16 | Post 16 | Total | 11-16 | Post 16 | Total | 2012 | 35 | 56.5 | 59.4 | [26 empty] | Description: | Some standards met but some areas not accessible
[5 empty] | 2017 | 74.4493 |  |  | 58.891 |  |  | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1381 | 45.7529 | 0 | 0 | D1 |  | 1 |  | 1 |  |  |  | Supplementary Area | 0 | 0 | - |  |  |  | 2008 / 2009 | 864 | 0 | 864 | 1050 | 0 | 1050 | 0 | 0 | 0 | 186 | 0 | 186 | 2013 | 46 | 56.1 | 59.2 | [5 empty] | Historical Catchment Analysis (Spring Census)
Telephone No.:- | T: 01432 357371 F: 01432 263925 |  | School Cluster:- | Hereford District- Aylestone Business and Enterprise College | 2018 | Not Available |  |  | 74.4493 |  |  | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0457 | 48.4036 | 0 | 0 | D2 |  | 1 | [5 empty] | Non Net Area | 1199.3 | 1439.96 | 120.0667 |  |  |  | 2009 / 2010 | 761 | 0 | 761 | 900 | 0 | 900 | 0 | 0 | 0 | 139 | 0 | 139 | 2014 | 50 | 58.7 | 53.4 | [5 empty] | Catchment Analysis |  |  |  | 2010 | 2011 | 2012 | 2013 | 2014
[5 empty] | 2019 | Not Available |  |  | Not Available |  |  | 2018 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | D3 | [7 empty] | Total Gross Building Area | 4175.55 | 6575.772 | 157.4828 |  |  |  | 2010 / 2011 | 689 | 0 | 689 | 750 | 0 | 750 | 0 | 0 | 0 | 61 | 0 | 61 | [12 empty] | Total in Catchment | 1076 | 1029 | 1001 | 1059 | 1063
[9 empty] | Not Available |  |  | 2019 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [15 empty] | 2011 / 2012 | 605 | 0 | 605 | 750 | 0 | 750 | 0 | 0 | 0 | 145 | 0 | 145 | KS4 Exam Results and Progress (2014) | [11 empty] | Number at School from Catchment | 516 | 451 | 409 | 391 | 347
School Type:- | Community |  | Building Number:- | EKAH | Total | 887.7218 | [5 empty] | Totals | 1.8785 | 0 | 10.3491 | 348.4943 | 5.9928 | 2.3049 | 3.1808 | 95.77 | 2.328 | 5.1861 | 88.1637 | 190.7332 | 0 | 0 | *Note the information noted above has been extracted from the EFA survey focusing on elements that are C & D rated. Items with an A or B rating have been excluded. The numbers reference the quantity of elements that the survey has picked up within the relevant category | [7 empty] | Total Gross Site Area | 35366.25 | 62062 | 175.4837 |  |  |  | 2012 / 2013 | 551 | 0 | 551 | 750 | 0 | 750 | 0 | 0 | 0 | 199 | 0 | 199 | [12 empty] | Percentage at School from Catchment | 67.8055 | 65.4572 | 67.6033 | 70.9619 | 72.5941
Current Capacity (11-16):- | 450 |  | Site Area:- | 62062 | [30 empty] | Net Site Area (less the building area) | 31190.7 | 55486.228 | 177.8935 |  |  |  | 2013 / 2014 | 478 | 0 | 478 | 750 | 0 | 750 | 0 | 0 | 0 | 272 | 0 | 272 | Number of pupils at end of KS4 |  |  |  | 113 | [7 empty] | Percentage of Catchment Going to School | 47.9554 | 43.829 | 40.8591 | 36.9216 | 32.6435
Current Capacity (Post 16):- | 0 | [10 empty] | Total Potential Expenditure - Local Authority (£000) | [6 empty] | 642.4885 | [22 empty] | Current Occupancy | 441 | 0 | 441 | 450 | 0 | 450 | 0 | 0 | 0 | 9 | 0 | 9 | Percentage achieving 5 A*-C GCSEs (or equivalents) including English and maths GCSEs |  |  |  | 50
Current Capacity (Total):- | 450 |  |  |  | Key Elements of Forecast Maintenance | [29 empty] | Key Information (based on Building Bulletin 103) | [19 empty] | Percentage achieving A*-C in English and maths GCSEs |  |  |  | 51 |  |  |  |  | Catchment and Nearest School Comparison (Autumn Census 2014)
[5 empty] | Categories |  | Totals (£ 000) | [19 empty] | Key | [7 empty] | Number of Temporary Buildings on Site |  |  |  | 3 |  |  | Current Occupancy Summary (Autumn Census 2014) | [12 empty] | Percentage of pupils achieving the Ebacc |  |  |  | 19 | [7 empty] | Catchment vs Nearest School | Catchment | Nearest
[5 empty] | External Grounds |  | 1.8785 |  |  |  |  | Total Potential Expenditure - School (£000) | [6 empty] | 111.893 | [7 empty] | Condition grade | Definition |  |  |  | Priority rating | Definition |  | Number of Classrooms in Temporary Buildings |  |  |  | 1 |  |  | Year Group | NOR |  |  | Shortfall |  |  | Surplus | [5 empty] | Percentage of pupils achieving 5+ A*-C grade GCSEs (or equivalent) |  |  |  | 63 | [7 empty] | NOR | 441 | 441
[5 empty] | Roof Works |  | 358.8435 | [27 empty] | Percentage of Recommended Pupil Toilets |  |  |  | 154.1667 |  |  | Seven | 70 |  |  | 0 |  |  | 20 | [5 empty] | Percentage of pupils achieving 5+ A*-G grade GCSEs (or equivalent) |  |  |  | 96 | [7 empty] | Total in Area | 1065 | 604
[5 empty] | External Walls |  | 8.2978 | [19 empty] | A Good | Performing as intended and operating efficiently |  |  |  | 1 | Immediate or year 1 remedial action required | [8 empty] | Eight | 72 |  |  | 0 |  |  | 18 | [5 empty] | Percentage of pupils making expected progress in English |  |  |  | 67 | [7 empty] | Number at School from Area | 334 | 176
[5 empty] | Windows and Doors |  | 98.9508 | [34 empty] | Nine | 102 |  |  | 12 |  |  | 0 | [5 empty] | Percentage of pupils making expected progress in maths |  |  |  | 63 | [7 empty] | Percentage at School | 75.737 | 39.9093
[5 empty] | Internal Works |  | 7.5141 | [19 empty] | B Satisfactory | Performing as intended but exhibiting minor deterioration |  |  |  | 2 | Year 1-2 remedial action required | [8 empty] | Ten | 89 |  |  | 0 |  |  | 1 | [5 empty] | Average point score |  |  |  | 312.5 | [7 empty] | Percentage of area going to School | 31.3615 | 29.1391
Asset Summary |  |  |  |  | Mechanical and Electrical |  | 278.8969 | [34 empty] | Eleven | 108 |  |  | 18 |  |  | 0
[5 empty] | Other (e.g. ancillary buildings) |  | 0 | [19 empty] | C Poor | Exhibiting major defects and/or not operating as intended |  |  |  | 3 | Year 3-5 remedial action required | [8 empty] | Twelve | 0 |  |  | 0 |  |  | 0 | [5 empty] | Latest Ofsted Report Date:- |  | 2011-10-12
Asset Value - Insurance (£000):- |  | 14458.891 | [39 empty] | Thirteen | 0 |  |  | 0 |  |  | 0 | [5 empty] | Ofsted Result:- |  | Good
Asset Value - Land (£000):- |  | Not Known | [24 empty] | D Bad | Life-expired and/or at serious risk of imminent failure | [13 empty] | Total | 441 |  |  | 0 |  |  | 9
Land Owner:- |  | Owned by the Local Authority | [37 empty] | Category | Areas Included
[40 empty] | Basic Teaching Spaces | General Classrooms, ICT Rooms, Art Rooms, Science Laboratories, DT Rooms, Music Rooms
[40 empty] | Hall and Studio | Halls, Dining Areas, Stage
Lease Agreement / Notes:- |  | Not Known | [37 empty] | Storage | Coats and Bags, Teaching, Specialist, PE Equipment, Bulk Stock, Cleaning, Caretakers and Maintenance, Tables and Chairs, Staging, Mobility Equipment, Science Prep Room
[40 empty] | Staff and Admin | Heads and Staff Offices, Staff Room, Staff PPA,Reprographics Room, Sick Bay, Interview and Meeting Rooms, Secure Entrance
[40 empty] | Learning Resource | Library, Small Group Rooms, SENCO Office, Medical Inspection Room, Music Practise Room, SEN Classrooms, Kiln
[40 empty] | Supplementary Area | Any other specialist area at the school e.g. Swimming Pool
[40 empty] | Non Net Area | Pupil and Staff Toilets, Accessible Toilets, Hygiene Room, Kitchen, Corridors, Server Room, Boilers
Asset value and insurance value has been queried by school and being investigated by Herefordshire councils estates team.

## Feedback
|  | Aylestone Business and Enterprise College |  |  | Aylestone Business and Enterprise College |  |  | Aylestone Business and Enterprise College
|  | Feedback Form |  |  | Feedback Form |  |  | Feedback Form
General Information and Asset Summary |  |  | School Occupancy Summary |  |  | Parental Preference
Do you believe the data to be accurate? |  |  | Do you believe the data to be a fair reflection of the current and historical position of the school? |  |  | Do you believe the data to be a fair reflection of the current and historical position of the school?
Yes | No |  | Yes | No |  | Yes | No
Additional comments: |  |  | Additional comments: |  |  | Additional comments:
Maintenance and Condition Summary |  |  | School Statistics |  |  | Disability Access
Do you believe the data to be a fair reflection of the maintenance and condition of the school? | [5 empty] | Do you believe the data to be a fair reflection of the environmental condition of the school?
Yes | No |  | Yes | No |  | Yes | No
Additional comments: |  |  | Additional comments: |  |  | Additional comments:
Suitability and Compliance Summary |  |  | Environmental Sustainability Condition |  |  | Any Other Comments
Do you believe the data to be a fair reflection of the suitability and compliance issues faced by the school? | [5 empty] | Additional comments about the information provided:
Yes | No |  | Yes | No
Additional comments: |  |  | Additional comments:
If you want assistance in completing this form please contact 01432 260920 |  |  | If you want assistance in completing this form please contact 01432 260920 |  |  | If you want assistance in completing this form please contact 01432 260920
Please return to Andy Hough, Head of Education and Development, Plough Lane, Hereford, HR4 0LE by 22 May 2015 |  |  | Please return to Andy Hough, Head of Education and Development, Plough Lane, Hereford, HR4 0LE by 22 May 2015 |  |  | Please return to Andy Hough, Head of Education and Development, Plough Lane, Hereford, HR4 0LE by 22 May 2015

## Asset summary
Building ref number:- | EKAH
Site Area:- | 62062
Building Type:- | Not Known
Asset Value (Insurance):- | 14458891
Asset Value (Land):- | Not Known
Land owner:- | Owned by the Local Authority
Lease agreement / notes:- | Not Known
DEC rating:- | C
Electric consumption 2014/child:- | 599.0167
Gas consumption 2014/child:- | 1475.7238

## Maintenance
Maintenance & Condition Summary | [5 empty] | BCIS Quarter | 3Q2012 | [11 empty] | Check | Main year totals | Summary year totals | Year | External Grounds |  | Roof Works |  | External Walls |  | Windows & Doors |  | Internal Works |  | Mechanical & Electrical |  | Other |  | BCIS quarter | BCIS uplift
Year survey undertaken |  | 2012-09-01 |  |  |  | BCIS Uplift | 1.1525 | [15 empty] | SC | LA | SC | LA | SC | LA | SC | LA | SC | LA | SC | LA | SC | LA | 1Q2009 | 1.1525
Survey company:- |  | Amey | [17 empty] | 557736.0987 | 557736.0987 | Backlog | 1555.8296 | 0 | 8966.1883 | 348494.3049 | 3457.3991 | 2304.9327 | 3180.8072 | 95769.9552 | 2327.9821 | 5186.0987 | 32096.1883 | 54396.4126 | 0 | 0 | 2Q2009 | 1.1898
[20 empty] | 63304.9776 | 63304.9776 | 2015 | 322.6906 | 0 | 1382.9596 | 0 | 2535.426 | 0 | 0 | 0 | 0 | 0 | 16883.6323 | 42180.2691 | 0 | 0 | 3Q2009 | 1.1898
[20 empty] | 58891.0314 | 58891.0314 | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13138.1166 | 45752.9148 | 0 | 0 | 4Q2009 | 1.2123
[6 empty] | Year covered? | Y | Y | Y | Y | N | N | School Costs | [6 empty] | 74449.3274 | 74449.3274 | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26045.7399 | 48403.5874 | 0 | 0 | 1Q2010 | 1.2297
Category | Ref | Element | Recommended Works |  |  | Estimated Work Cost | Backlog | 2015 | 2016 | 2017 | 2018 | 2019 | Backlog | 2015 | 2016 | 2017 | 2018 | 2019 |  | 58891.0314 | 58891.0314 | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13138.1166 | 45752.9148 | 0 | 0 | 2Q2010 | 1.1789
[20 empty] | 74449.3274 | 74449.3274 | 2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26045.7399 | 48403.5874 | 0 | 0 | 3Q2010 | 1.1735
|  | 2.1 EXTERNAL GROUNDS | [34 empty] | 4Q2010 | 1.1682
|  | SURFACES | [19 empty] | Individual Category totals | 1878.5202 | 0 | 10349.148 | 348494.3049 | 5992.8251 | 2304.9327 | 3180.8072 | 95769.9552 | 2327.9821 | 5186.0987 | 127347.5336 | 284889.6861 | 0 | 0 | 1Q2011 | 1.1735
g | 2.1.1 | Macadam | Located next to manhole covers inside large playground area the ground surface has raised in parts see photographs. This is causing a trip hazard. It is recommended to investigate the condition of the drain pipe which appear to pass underneath the playground and may be damaged. | KC | 2 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 2Q2011 | 1.1525
g | 2.1.2b | Macadam | To the side of Home Economic Original Part EKAH/FA concrete paving slabs are dislodged and uneven. Remove and re-lay. See photos in appendix. | KD | 3 | 300 | 300 | [5 empty] | 300 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Summary category totals | Main category totals | Check | [11 empty] | 3Q2011 | 1.1682
g | 2.1.2c | Macadam | Concrete steps in front of Library Original Part EKAH/CA are loose. Remove and relay. All mortars joints to steps to be re-pointed throughout. | KD | 2 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 4Q2011 | 1.1525
g | 2.1.2d | Macadam | Steps leading out of B Block Main Teaching EKAH/BA and out onto grassed areas area loose and unsecure. Remove and re-lay using fresh mortar. | KD | 2 | 350 | 350 | [5 empty] | 350 | 0 | 0 | 0 | 0 | 0 |  |  | External Grounds |  | 1878.5202 | 1878.5202 | [12 empty] | 1Q2012 | 1.1953
|  | FENCES,WALLS,BOUNDARY |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Roof Works |  | 358843.4529 | 358843.4529 | [12 empty] | 2Q2012 | 1.1174
g | 2.1.5 | Metal gates | Gates are in reasonable condition but require decorating. | KF | 3 | 280 | 0 | 280 |  |  |  |  | 0 | 280 | 0 | 0 | 0 | 0 |  |  | External Walls |  | 8297.7578 | 8297.7578 | [12 empty] | 3Q2012 | 1.1525
|  | 2.2 ROOFS AND FEATURES - EKAH/BA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Windows & Doors |  | 98950.7623 | 98950.7623 | [12 empty] | 4Q2012 | 1.1473
r | 2.2.1 | Main roof - pitched | Roof covering approximately 15 years old. Build up of lichen in areas. The roof covering is nearing the end of its design life. Water ingress was noted within room 29 - Mrs Hendry, outside the landing of room 29 and staff room 25a (see internal section for further details). It is recommended that a full intrusive survey is undertaken to the roof covering establishing the construction method and u-values. It could not be determined at the time of the survey whether or not the roof is insulated or not. An estimated cost has been given to upgrade the covering and to provide new insulation to meet current regulations. | AB | 2 | 232890 | 232890 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Internal Works |  | 7514.0807 | 7514.0807 | [12 empty] | 1Q2013 | 1.0983
r | 2.2.2 | Main roof - flat | Water ingress has been reported to the male and female toilets adjacent to B Block Sports Hall EKAH/BB. No access was available onto the roof. It is recommended to undertake a full intrusive survey of the roof covering and construction build up. Water has been reported to be ingressing via the roof lights. | AA | 2 | 5000 | 5000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Mechanical & Electrical |  | 412237.2197 | 412237.2197 | [12 empty] | 2Q2013 | 1.089
r | 2.2.3 | Roof lights | Single glazed units do not conform to current regulations. It is recommended to remove and replace these units with triple glazed fittings that conform to current standards and regulations. | AD | 2 | 3500 | 3500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Other |  | 0 | 0 | [12 empty] | 3Q2013 | 1.0983
r |  |  | Water staining and ingress found around roof light located in staff room 25a. Condition of roof detailing around window light unknown, further investigation required. | AD | 2 | 1200 | 1200 | [5 empty] | 1200 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 4Q2013 | 1.0798
r | 2.2.4 | Gutters | Clean out and remove blockages. Gutters adjacent to main front entrance are blocked causing wood fascia/soffits boards to rot. | AE | 2 | 800 | 800 | [5 empty] | 800 | 0 | 0 | 0 | 0 | 0 |  |  | Total |  | 887721.7937 | 887721.7937 | [12 empty] | 1Q2014 | 1.0447
|  | 2.3 EXTERNAL ELEVATIONS - EKAH/BA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 2Q2014 | 1.0198
e | 2.3.1 | Walls | Build up of ivy towards the west end of the building. Generally the walls appear to be in good condition. Minor pointing required. | DA | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 3Q2014 | 1.028
w | 2.3.2 | Windows | Cracked glazing to main hall and missing putty. Remove and replace glazing and putty. | DC | 3 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 4Q2014 | 1.0078
e | 2.3.3 | Slate cladding | A number of slates are loose/slipped. A number of slates have deteriorated with edges weathered. It is advised to remove and replace slates to the elevation. | DA | 3 | 800 | 800 | [5 empty] | 800 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 1Q2015 | 1
e | 2.3.5 | Timber cladding | Timber slats have bowed due to heat from sun. Remove and replace timbers boards. | DA | 3 | 800 | 800 | [5 empty] | 800 | 0 | 0 | 0 | 0 | 0
|  | 2.4 INTERNAL - EKAH/BA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | 1st floor |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
i | 2.4.11 | Floor covering | Vinyl flooring is damaged to room 29. In rooms 26/27 the floor covering is heavily soiled and can do with being replaced. | BA | 2 | 1500 | 1500 | [5 empty] | 1500 | 0 | 0 | 0 | 0 | 0
i | 2.4.12 | Doors | Ironmongery generally is loose. Fittings need to be re-adjusted and securely fixed. | EB | 3 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
|  | 2.5 ROOFS AND FEATURES - B Block Sports Hall EKAH/BB |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
r | 2.5.2 | Roof lights | Water ingress has been reported to this building but the location could not be verified. Glazing to roof lights were cracked, approximately 8no. Panes require replacing. | AD | 3 | 2500 | 2500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | 2.8 ROOFS AND FEATURES - Home Economics Original Part EKAH/FA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
r | 2.8.1 | Main roof | Water ingress has only been reported around the perimeter drainage outlets. The roof covering generally is poorly installed, with loosely laid lap joints and poor patch repairs. The roof covering has began to blister in various locations indication water penetrating through. It could not be confirmed whether insulation and a vapour control layer has been installed. For a longer term solution it is recommended to remove the roof covering and increase insulation. | AA | 1 | 55000 | 55000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
r | 2.8.1b | Timber hatch leading to main roof | Timber cladding is defective and rotten. Remove and replace defective slats. | AF | 2 | 1000 | 1000 | [5 empty] | 1000 | 0 | 0 | 0 | 0 | 0
r | 2.8.2 | Gutters | We have been informed these outlets get block frequently causing water to enter into the building. In our internal inspection the roof outlets run internally inside the building. Some repair works have been undertaken in the past but it has been reported water still comes in from this location during heavy down pours. It is recommended as part of the replacement of the roof covering to re-detail the internal outlets and remove the chances of cold-bridging. | AE | 2 | 3500 | 3500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | 2.9 EXTERNAL ELEVATIONS - Home Economics Original Part EKAH/FA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
w | 2.9.2 | Windows | The windows are approximately 30 years old and are considered past there maintainable life span. Mastic beads throughout are defective, water ingress has been reported through a number of windows internally. We recommend all windows are replaced in powder coated aluminium windows that meet current standards and regulations. | DC | 2 | 70000 | 70000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
w | 2.9.3 | Doors | Reasonable condition. If external windows are upgraded it is recommended to include the front door and screen as well. | DC | 2 | 3500 | 3500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | 2.10 INTERNAL - Home Economics Original Part EKAH/FA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | Ground floor |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
i | 2.10.4 | Floor covering | Within room C1 food technology the floor covering is in very poor condition. Remove and replace. | BA | 3 | 4500 | 4500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | 2.15 EXTERNAL ELEVATIONS - CA1 & CA2 Elliott Music Block A&B Porta Cabin |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
i | 2.15.1 | Downpipes | Downpipe roof connection missing. Replace with new. | AE | 3 | 20 | 20 | [5 empty] | 20 | 0 | 0 | 0 | 0 | 0
|  | 2.17 ROOFS AND FEATURES - Library Original Part EKAH/CA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
r | 2.17.1 | Roof | A build up of debris on the roof space. A number delaminated tiles approximately 20nr. Remove debris and replace missing/delaminated tiles. | AB | 3 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
|  | 2.18 EXTERNAL ELEVATIONS - Library Original Part EKAH/CA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
r | 2.18.1 | Fascia and Soffits | Approximately 20LM of rotten and defective boarding. Remove and replace and decorate thereafter. | AF | 3 | 300 | 300 | [5 empty] | 300 | 0 | 0 | 0 | 0 | 0
r | 2.18.2 | Downpipes | Missing sections, 5no. 12LM blocked outlets. Replace and clean out outlets. | AF | 3 | 80 | 80 | [5 empty] | 80 | 0 | 0 | 0 | 0 | 0
e | 2.18.4 | Walls | Redecoration required. | DA | 3 | 2000 | 2000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
w | 2.18.5 | Windows | Redecoration required. | DC | 3 | 1000 | 1000 | [5 empty] | 1000 | 0 | 0 | 0 | 0 | 0
w | 2.18.6 | Doors | Redecoration required. | DC | 3 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
|  | 2.24 EXTERNAL ELEVATIONS - C.D.T Block Original Part EKAH/EA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
w | 2.24.2 | Windows | A number of windows are suffering from wet rot, with defective beads, cills, missing putty. Approximately 12no. windows require repair works. | DC | 3 | 9600 | 9600 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
w | 2.24.2c |  | 12no. Window panes are defective with clear signs of condensation build up between cavity gap. Remove and replace windows panes. | DC | 3 | 960 | 960 | [5 empty] | 960 | 0 | 0 | 0 | 0 | 0
r | 2.24.4 | Down pipes | Metal brackets have corroded. Remove and replace missing downpipes and brackets. | AF | 3 | 150 | 150 | [5 empty] | 150 | 0 | 0 | 0 | 0 | 0
|  | 2.32 ROOFS AND FEATURES - Broadlands Cottage EKAH/HA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
r | 2.32.1 | Roof | There is a build up of lichen to the West elevation. Approximately 5-10 slipped/loose slates. It is recommended to replace them. | AA | 3 | 1500 | 1500 | [5 empty] | 1500 | 0 | 0 | 0 | 0 | 0
r | 2.32.2b | Roof lights | Timber frame is defective and requires redecorating. No access obtainable into area where roof light was fixed. It is recommended to upgrade roof light with a double glazed fitting which is also low maintenance. | AD | 2 | 1000 | 1000 | [5 empty] | 1000 | 0 | 0 | 0 | 0 | 0
r | 2.32.3 | Chimney | Mortar repairs required. Approximately 6LM. | AC | 3 | 1200 | 0 | 1200 |  |  |  |  | 0 | 1200 | 0 | 0 | 0 | 0
r | 2.32.4 | Lead flashing | Missing mortar joints to front West elevation. Re-point. Inspection taken from ground level. | AF | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
r | 2.32.5 | Gutters | Delamination in gutter line. Remove and replace gutter brackets. | AF | 3 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
|  | 2.33 EXTERNAL ELEVATIONS - Broadlands Cottage EKAH/HA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
e | 2.33.1 | Walls | Minor mortar repairs. | DA | 3 | 100 | 0 | 100 |  |  |  |  | 0 | 100 | 0 | 0 | 0 | 0
e | 2.33.2b |  | Redecoration required. | DA | 3 | 500 | 0 | 500 |  |  |  |  | 0 | 500 | 0 | 0 | 0 | 0
e | 2.33.4 | Lintels | Above small single glazed timber window to West elevation, brick arch has slightly dropped from its original position. It is recommended to monitor this movement. | DA | 3 | 1000 | 1000 | [5 empty] | 1000 | 0 | 0 | 0 | 0 | 0
|  | Small outhouse building against to main block |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
e | 2.33.6 | Walls | Delaminated bricks to corner of building and adjacent to door BC10. Cut out bricks and replace with new to prevent further deterioration. To the North elevation a number of bricks faces are defective and blown. Cut out and replace. Rake out and remove defective mortar approx 5LM. There is a severe build up of vegetation growing on the building facade. Remove all roots/vegetation. | DA | 3 | 1600 | 0 | 1600 |  |  |  |  | 0 | 1600 | 0 | 0 | 0 | 0
w | 2.33.8 | Windows | New external putty required. Redecorate all windows. | DC | 3 | 100 | 100 | [5 empty] | 100 | 0 | 0 | 0 | 0 | 0
r | 2.33.9 | Downpipes | Missing downpipe and outlet blocked. Replace missing downpipe and un-block outlet removing vegetation. | AF | 3 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
|  | 2.35 ROOFS AND FEATURES - Humanities Block Original Part EKAH/KA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
r | 2.35.4 | Gutters | Build up of vegetation. Clean out. | AF | 3 | 150 | 150 | [5 empty] | 150 | 0 | 0 | 0 | 0 | 0
|  | 2.36 EXTERNAL ELEVATIONS - Humanities Block Original Part EKAH/KA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 2.36.6 | Ventilation grills | Plastic air vents are broken/missing. Remove and replace 10no. | AF | 3 | 50 | 50 | [5 empty] | 50 | 0 | 0 | 0 | 0 | 0
|  | Block B Main Teaching EKAH/BA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Ventilation |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.1 | Boys Changing and Showers 37 | 12" Axial extract fan at high level in changing room wall with remote manual controller. The unit is inoperable and requires replacement. | GE | 2 | 600 | 600 | [5 empty] | 600 | 0 | 0 | 0 | 0 | 0
m | 3.15.2 | Boys Changing and Showers 37 | 430x440 non-vision transfer grilles to Gym 30.Damage consists of bend louvre blades. Performance unaffected however replacement should be considered if aesthetics are a concern in this area. | GE | 4 | 800 | 0 |  |  | 400 |  | 400 | 0 | 0 | 0 | 400 | 0 | 400
m | 3.15.3 | Gymnasium 30 | Corridor to gym non vision transfer grille (440x440mm). Corridor side louvres have suffered significant impact damage. Performance unaffected however replacement should be considered if aesthetics are a concern in this area. | GE | 4 | 400 | 0 |  |  | 200 |  | 200 | 0 | 0 | 0 | 200 | 0 | 200
m | 3.15.4 | Lockers 63 | Xpelair 100mmm window mounted axial extract fan. Recommend replacing the extract fan with a simple circular window ventilator since powered extract ventilation is not required in this area. | GE | 3 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
m | 3.15.5 | Science Store 80 | Room extract system comprising ceiling mounted grille and axial extract fan (Vent Axia) Local wall mounted 2 speed fan controller (Vent Axia). The extract system is not operational although in good condition. Allowance made to investigate the fault. | GE | 2 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
m | 3.15.6 | Female Staff WC 97 | Vent axia '6X' window mounted extract fan with local control via switched fused connection unit. The existing unit is operational however is now beyond its anticipated CIBSE life expectancy and renewal of the unit should be considered. | GE | 3 | 250 | 250 | [5 empty] | 250 | 0 | 0 | 0 | 0 | 0
m | 3.15.7 | Science Classroom 57 | 12" Xpelair window mounted extract fan in high level classroom windows. Controls situated in room 56. The fuse within the SFCU serving these fans has been removed rendering them inoperable. It is assumed that this is due to a fault and hence an allowance has been made for investigation. | GE | 3 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
m | 3.15.8 | Modern Languages Classroom 108 | 12" Xpelair wall mounted extract fan with local wall mounted controller. The unit is not operational. The purpose of this extract was unclear at the time of the survey since it discharges from the classroom to the adjacent corridor. | GE | 3 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
m | 3.15.9 | Girls Changing Rooms 33 | Two extract systems - 1 serves changing area and 1 serves showers. Systems compose 450mm sq. extract grilles mounted in ceiling grid. It is assumed that these are served by ducted extract fans. Local isolators are provided for each system. The shower extract system is not operational. No access could be gained to the extract fans (assumed to be a ducted unit above the false ceiling). Recommend further investigation of this system. | GE | 2 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
m | 3.15.10 | Girls Changing Rooms 33 | Non-vision transfer grilles to corridor. Damage consists of bend louvre blades on corridor side. Performance unaffected however replacement should be considered if aesthetics are a concern in this area. | GE | 4 | 400 | 0 |  |  | 200 |  | 200 | 0 | 0 | 0 | 200 | 0 | 200
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.11 | General | The majority of the LTHW heating distribution system comprises original steel flow and return pipework most of which is concealed within the building fabric. Given the age of the construction any original LTHW distribution pipework should be considered for replacement. It is understood that the primary flow and return pipework situated within the floor duct below the main corridor has undergone recent refurbishment due to failure. No record information relating to the system could be found therefore it is recommended that a further assessment / survey of the system be undertaken in order to ascertain its condition and scope. | GB | 3 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.12 | Boys Changing and Showers 37 | Pressed steel panel radiator in LST casing with TRV. Also a single low level steel pipe coil is provided. Two number LST casings are badly damaged and no longer correctly secured to the wall. The pipe coil is in average condition for its age however CIBSE plant life expectancies would suggest that this item is now overdue for replacement. | GB | 2 | 800 | 800 | [5 empty] | 800 | 0 | 0 | 0 | 0 | 0
m | 3.15.13 | Corridors and WCs generally | Mixture of exposed LST cased steel panel and original cast iron sectional radiators. LTHW derived from original screwed/socketed steel pipework installation. * Original steel pipework and cast iron radiators. Much of the existing pipework is run within floor ducts which were not accessed at the time of the survey although it is understood some sections of this installation have been replaced due to failure. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. We also note that where TRVs were fitted to corridor heat emitters these are missing or broken and would recommend that these are either replaced with anti vandal models or lock shield valves to prevent tampering and damage. | GB | 3 | 9600 | 0 |  |  | 4800 |  | 4800 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.14 | IT Room 21 | Vertical cased fan convector. Fan convector casing is starting to display wear and tear associated with its age. Continue to carry out normal maintenance activities with a view to replacing the unit at end of life. | GB | 4 | 2400 | 0 |  |  | 1200 |  | 1200 | 0 | 0 | 0 | 1200 | 0 | 1200
m | 3.15.15 | Inclusion Unit 18 | Vertical cased fan convector. Fan convector casing is starting to display wear and tear associated with its age. Continue to carry out normal maintenance activities with a view to replacing the unit at end of life. | GB | 4 | 2400 | 0 |  |  | 1200 |  | 1200 | 0 | 0 | 0 | 1200 | 0 | 1200
m | 3.15.16 | Classroom 28 | Vertical cased fan convector. Light damage to casing due to impact. Continue to carry out normal maintenance activities with a view to replacing the unit at end of life. | GB | 4 | 2400 | 0 |  |  | 1200 |  | 1200 | 0 | 0 | 0 | 1200 | 0 | 1200
m | 3.15.17 | Gymnasium 30 | Vertical cased fan convectors in gym store with high and low level grilles to gym. Units operational however grilles are damaged due to impact. Continue to carry out normal maintenance activities with a view to replacing the unit at end of life. Recommend the use of more robust grilles when replaced. | GB | 4 | 3600 | 0 |  |  | 1800 |  | 1800 | 0 | 0 | 0 | 1800 | 0 | 1800
m | 3.15.18 | Main Entrance 1 | 2 No. original horizontal cased floor standing fan convectors, 1 No. SPC Belgravia horizontal cased fan convector. The 2 No. original horizontal cased fan convectors form a part of the original LTHW heating distribution and as such are in a poor state of repair. The SPC Belgravia appears to be some 10 years old and as such it is anticipated that this unit would not require anything other than general cleaning and maintenance in the medium term. | GB | 3 | 2000 | 2000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.19 | Head Teacher Kitchenette 10 | Original cast iron sectional radiator. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 600 | 600 | [5 empty] | 600 | 0 | 0 | 0 | 0 | 0
m | 3.15.19 | Head Teacher Office 9A | Original cast iron sectional radiator. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 800 | 800 | [5 empty] | 800 | 0 | 0 | 0 | 0 | 0
m | 3.15.20 | Science Classroom 83 | Original horizontal cased floor standing fan convector. CIBSE plant life expectancies estimate 30 years for pipework and 15 for fan convectors. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. Fan convectors also date back to the original heating installation and as such are overdue renewal. It is understood that this classroom is due to be fully refurbished during Summer 2012. | GB | 3 | 2000 | 2000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.21 | Science Classroom 83 | Original pressed steel panel radiator and associated valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. It is understood that this classroom is due to be fully refurbished during Summer 2012. | GB | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m | 3.15.22 | Science Store 87 | Original cast iron sectional radiator and associated valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m | 3.15.23 | Science Classroom 88 | Original horizontal cased floor standing fan convector. CIBSE plant life expectancies estimate 30 years for pipework and 15 for fan convectors. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. Fan convectors also date back to the original heating installation and as such are overdue renewal. | GB | 3 | 2000 | 2000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.24 | Science Classroom 88 | Original cast iron sectional radiator and associated valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m | 3.15.25 | Science Classroom 82 | Original horizontal cased floor standing fan convector. CIBSE plant life expectancies estimate 30 years for pipework and 15 for fan convectors. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. Fan convectors also date back to the original heating installation and as such are overdue renewal. | GB | 3 | 2000 | 2000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.25 | Science Classroom 78 | Original concealed vertical cased FCU (sited in room 80) with high and low level wall grilles room side. CIBSE plant life expectancies estimate 30 years for pipework and 15 for fan convectors. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. Fan convectors also date back to the original heating installation and as such are overdue renewal. | GB | 3 | 1000 | 1000 | [5 empty] | 1000 | 0 | 0 | 0 | 0 | 0
m | 3.15.26 | Science Classroom 78 | Original cast iron sectional radiator and associated valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 1000 | 1000 | [5 empty] | 1000 | 0 | 0 | 0 | 0 | 0
m | 3.15.27 | Room 96 | Original cast iron sectional radiator and associated valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m | 3.15.28 | Science Classroom 88A | Original cast iron sectional radiator and associated valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. Minor leakage noted at valve connections. | GB | 2 | 1200 | 1200 | [5 empty] | 1200 | 0 | 0 | 0 | 0 | 0
m | 3.15.29 | Science Staff Room 93 | Original cast iron sectional radiator and associated valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m | 3.15.30 | Modern Languages Classroom 108 | SPC Belgravia horizontal cased floor standing fan convector. The existing fan convector is in average condition for its age however with reference to CIBSE plant life expectancies it is recommended that renewal of this unit be considered in the medium term. | GB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.15.31 | Modern Languages Classroom 110 | SPC Belgravia horizontal cased floor standing fan convector. The existing fan convector is in average condition for its age however with reference to CIBSE plant life expectancies it is recommended that renewal of this unit be considered in the medium term. | GB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.15.32 | Academic Learning Coaches 112 | SPC Belgravia horizontal cased floor standing fan convector. It is assumed that the casing has been repainted (black) as a part of the recent refurbishment in this area. The existing fan convector although repainted is in average condition for its age however with reference to CIBSE plant life expectancies it is recommended that renewal of this unit be considered in the medium term. | GB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.15.33 | Science Classroom 57 | SPC Belgravia horizontal cased floor standing fan convector. The existing fan convectors are in average condition for their age however with reference to CIBSE plant life expectancies it is recommended that renewal of this unit be considered in the medium term. | GB | 3 | 4000 | 0 |  |  | 2000 |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.34 | Science Classroom 54 | SPC Belgravia horizontal cased floor standing fan convector. The existing fan convectors are in average condition for their age however with reference to CIBSE plant life expectancies it is recommended that renewal of this unit be considered in the medium term. | GB | 3 | 4000 | 0 |  |  | 2000 |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.35 | Science Classroom 48 | SPC Belgravia horizontal cased floor standing fan convector. The existing fan convectors are in average condition for their age however with reference to CIBSE plant life expectancies it is recommended that renewal of this unit be considered in the medium term. | GB | 3 | 4000 | 0 |  |  | 2000 |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.36 | Science Classroom 59 | SPC Belgravia horizontal cased floor standing fan convector. The existing fan convectors are in average condition for their age however with reference to CIBSE plant life expectancies it is recommended that renewal of this unit be considered in the medium term. | GB | 3 | 4000 | 0 |  |  | 2000 |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.37 | Girls Changing Rooms 33 | Original low level steel pipe coils with associated valves. The pipe coils are in average condition for their age however CIBSE plant life expectancies would suggest they are now overdue for renewal. | GB | 3 | 1000 | 1000 | [5 empty] | 1000 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | Domestic Water & Drainage |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.38 | General | Domestic Hot and Cold water services are derived from a boosted system and emanate from the basement boiler room. Distribution pipework was largely concealed within the building fabric and could therefore not be assessed. Given the age of the construction any original hot and cold water and natural gas distribution pipework should be considered for replacement. No record information relating to the system could be found therefore it is recommended that a further assessment / survey of the system be undertaken in order to ascertain its condition and scope. | GD/GG | 3 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.15.39 | Science Classroom 57 | 15mm H&C capped off at low level below whiteboard. The full extent of the hot and cold water services pipework could not be determined in this area however it is assumed that these capped services are creating dead legs on the existing system and as such further investigating/remediation is recommended. | GD | 1 | 100 | 100 | [5 empty] | 100 | 0 | 0 | 0 | 0 | 0
m | 3.15.40 | Science Classroom 54 | Cold water outlet (tap) over belfast sink dripping continuously. | GD | 2 | 50 | 50 | [5 empty] | 50 | 0 | 0 | 0 | 0 | 0
m | 3.15.41 | Main School Kitchen 69 | Whereas the remainder of mechanical services within the kitchen have been recently replaced, the hot and cold water services pipework appears original. Original hot and cold water services pipework. CIBSE plant life expectancies estimate 35 years for pipework and 15-20 for valves. As such the whole of the hot and cold distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GD | 3 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | B Block Sports Hall EKAH-BB |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | Ventilation |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.16.01 | Sports Hall 42 | Original ducted supply and extract ventilation plant sited at high level in store area 42. Supply AHU incorporates LTHW heating coil, BMS space temperature sensor wall mounted in hall above store. Manual on/off control provided for ventilation plant wall mounted in store area 42. Original ventilation plant. CIBSE plant life expectancies estimate 20 years for ductwork. The installation appears to be in very good condition given its age. As such the whole of the installation should be properly accessed to establish its condition with a view to potential renewal. | GE | 3 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Home Economics EKHA-FA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Ventilation |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.01 | Home Economics Classroom 121 | Vent Axia wall mounted 6" axial extract fan with local controller. Note these form a part of a builders work canopy situated above each domestic cooker/hob. The units are original and 4 No. were no longer operational at the time of inspection. All units displayed a build up of fats/grease from cooking since they are unfiltered simple extract fans. Recommend replacing with domestic cooker hoods. | GE | 2 | 1500 | 1500 | [5 empty] | 1500 | 0 | 0 | 0 | 0 | 0
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.02 | Heating general | LPHW is derived from Block B Main Teaching EKAH/BA heating system. The Science classrooms heating circuit is extended from the main block to serve this building. Given the age of the construction any original LTHW distribution pipework should be considered for replacement. No record information relating to the system could be found therefore it is recommended that a further assessment / survey of the system be undertaken in order to ascertain its condition and scope. | GB | 3 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.03 | Home Economics Classroom 121 | SPC Belgravia horizontal cased floor standing fan convector. The units appear to be some 15 years old and with reference to CIBSE plant life expectancies, are approaching end of life and should be considered for renewal. It is noted that the units form the ends of island units and therefore a builders work element should be allowed for in their replacement. | GB | 3 | 4000 | 0 |  |  | 2000 |  | 2000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.04 | Home Economics Room 124 | SPC Belgravia horizontal cased floor standing fan convector. The unit appears to be some 15 years old and with reference to CIBSE plant life expectancies, are approaching end of life and should be considered for renewal. | GB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.17.05 | Classroom 136 | SPC Belgravia horizontal cased floor standing fan convector. The unit appears to be some 15 years old and with reference to CIBSE plant life expectancies, are approaching end of life and should be considered for renewal. | GB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.17.06 | Classroom (IT) 137 | Original steel pipe coil and associated valves. Original steel heating installation. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 1200 | 0 |  |  | 600 |  | 600 | 0 | 0 | 0 | 600 | 0 | 600
m | 3.17.07 | Classroom (IT) 129 | SPC Belgravia horizontal cased floor standing fan convector. The unit appears to be some 15 years old and with reference to CIBSE plant life expectancies, are approaching end of life and should be considered for renewal. | GB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.17.08 | Reprographics 126 | Original steel panel radiator, pipework, and valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m | 3.17.09 | Classroom (IT) 135 | SPC Belgravia horizontal cased floor standing fan convector. The unit appears to be some 15 years old and with reference to CIBSE plant life expectancies, are approaching end of life and should be considered for renewal. | GB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.17.10 | Common Areas | Original steel panel radiator, pipework, and valves. Original steel pipework and radiator. CIBSE plant life expectancies estimate 30 years for pipework and 25 for emitters. As such the whole of the LPHW distribution system where original is now beyond its maximum anticipated life expectancy and should be considered for replacement. | GB | 3 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Domestic Water & Drainage |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.11 | Hot and Cold Water Services General | In the absence of any record information it is assumed that the building's hot and cold water services are derived from Block B Main Teaching EKAH/BA. There are 2 No. decommissioned cold water storage cisterns within a rooftop plant room but these have been historically bypassed in order to provide direct supply to all outlets within the building. Given the age of the construction any original hot and cold water distribution pipework should be considered for replacement. No record information relating to the system could be found therefore it is recommended that a further assessment / survey of the system be undertaken in order to ascertain its condition and scope. | GD | 3 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Air Conditioning |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.12 | Classroom (IT) 123 | Cirrus 16 wall through wall console unit. The units are in very poor condition and of such an age that the manufacturer could no longer be traced. Recommend replacing with new unitary split heat pump system. | GF | 2 | 3000 | 3000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.13 | Classroom (IT) 137 | Daikin FT60GZV1NB wall mounted split type fan coil unit with infra red remote controller. The units are in a fair state of repair and operational however with reference to CIBSE plant life expectancies these units should be considered for replacement at 15 years. | GF | 4 | 6000 | 0 |  |  | 3000 |  | 3000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.14 | Classroom (IT) 129 | Daikin FAYP1008V1wall mounted split type fan coil unit with infra red remote controller. The units are in a fair state of repair and operational however with reference to CIBSE plant life expectancies these units should be considered for replacement at 15 years. | GF | 4 | 10000 | 0 |  |  | 5000 |  | 5000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.15 | Classroom (IT) 127 | Daikin FAYP1008V1wall mounted split type fan coil unit with infra red remote controller. The unit is in a fair state of repair and operational however with reference to CIBSE plant life expectancies these units should be considered for replacement at 15 years. | GF | 4 | 6000 | 0 |  |  | 3000 |  | 3000 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.17.16 | Classroom (IT) 135 | Mitsubishi Electric PKA-RP100KAL wall mounted split type fan coil units with infra red remote controller. The units are as new and should only require programmed maintenance and cleaning. Note the green LED on one of the unit fascia's was flashing at the time of inspection which normally signal that the unit requires inspection. | GF | 2 | 150 | 150 | [5 empty] | 150 | 0 | 0 | 0 | 0 | 0
m |  | Single Austin Hall T4 Porta Cabin |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.18.1 | Room 001 - LTHW Heating | The radiators are in good working order and should be for the next few years, however an allowance should be made for maintenance/painting over the next few years. | GB | 3 | 300 | 0 |  | 150 |  | 150 |  | 0 | 0 | 150 | 0 | 150 | 0
m |  | CA1 & CA2 Elliott Music Block A&B Porta Cabin |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.19.1 | Room 002 - Heating | The fan convector is in good working order and should be for the next few years, however nearing the end of its plant operational life expectancy. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 3 | 1600 | 0 |  | 800 |  | 800 |  | 0 | 0 | 800 | 0 | 800 | 0
m | 3.19.2 | Room 005 - Heating | The fan convector is in good working order and should be for the next few years, however nearing the end of its plant operational life expectancy. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 3 | 1600 | 0 |  | 800 |  | 800 |  | 0 | 0 | 800 | 0 | 800 | 0
m |  | Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.19.3 | Room 002 - Hot Water Services | The point of use hot water heater is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 3 | 1200 | 0 |  | 600 |  | 600 |  | 0 | 0 | 600 | 0 | 600 | 0
m | 3.19.4 | Room 005 - Hot Water Services | The point of use hot water heater is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 3 | 1200 | 0 |  | 600 |  | 600 |  | 0 | 0 | 600 | 0 | 600 | 0
m |  | Library Original Part EKAH/CA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.20.2 | Library - LTHW Radiators | The radiators are in good working order and should be for the next few years, however will require some maintenance/painting over the next few years. | GB | 3 | 800 | 0 |  | 400 |  | 400 |  | 0 | 0 | 400 | 0 | 400 | 0
m | 3.20.4 | Library plant room - Boiler | The boiler is currently in serviceable condition and should be serviceable for the next few years, but will require replacement after this period as it nears the end of its expected operational life. Replace units as necessary Allowance made for an annual expenditure. | GA | 3 | 1000 | 0 | 1000 |  |  |  |  | 0 | 1000 | 0 | 0 | 0 | 0
m | 3.20.5 | Library plant room - Boiler Flue's | The units are currently operating and should be for the next few years, however will require renewal after this period. Replace as necessary. | GI | 3 | 700 | 0 | 700 |  |  |  |  | 0 | 700 | 0 | 0 | 0 | 0
m | 3.20.6 | Library plant room - LTHW Pumps | Pumps are generally in good condition and should be serviceable for the next few years. Replace as necessary. | GB | 3 | 800 | 0 | 800 |  |  |  |  | 0 | 800 | 0 | 0 | 0 | 0
m | 3.20.7 | Library plant room - Gas Solenoid Valve | There is no Gas Solenoid Valve & panic button, improvement required. | GG | 1 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.20.8 | Library plant room - LTHW Pipework | The pipework insulation are generally require upgrade/improvement . | GB | 3 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m |  | Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.20.9 | Library - Hot Water Services | The point of use hot water heater is currently in good operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 3 | 1200 | 0 |  | 600 |  | 600 |  | 0 | 0 | 600 | 0 | 600 | 0
m | 3.20.10 | Library Plant room - Cold Water Tank | The cold water tank is currently operating, however requires upgrade/improvement as it nears the end of its expected life expectancy. Replace as necessary. | GD | 3 | 2000 | 0 |  | 1000 |  | 1000 |  | 0 | 0 | 1000 | 0 | 1000 | 0
m |  | C.D.T Original Part EKAH/EA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.22.7 | Plant room - Gas Solenoid Valve | There is no Gas Solenoid Valve & panic button, improvement required. | GG | 1 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m |  | Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.22.9 | Room 160A, 160B, & 169 - Hot Water Services | The point of use hot water heaters currently in good operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 3 | 1200 | 0 |  |  | 600 |  | 600 | 0 | 0 | 0 | 600 | 0 | 600
m | 3.22.10 | Rooms 169 | The point of use hot water heater is currently in good operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 3 | 1200 | 0 |  |  | 600 |  | 600 | 0 | 0 | 0 | 600 | 0 | 600
m |  | CA3, CA4, CA5 Elliott Art Block A,B,C Porta Cabin |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Ventilation |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.23.1 | Room 003 - Ventilation | The extract fan is in good working order and should be for the next few years, however after will need replacing as it nears the end of its expected life expectancy. Replace as necessary. | GE | 3 | 400 | 0 | 400 |  |  |  |  | 0 | 400 | 0 | 0 | 0 | 0
m |  | Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.23.3 | Room 004, 002 - Hot Water Services | The point of use hot water heater is currently in good operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 3 | 1200 | 0 |  | 600 |  | 600 |  | 0 | 0 | 600 | 0 | 600 | 0
m | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | English Block Original Part EKAH/IA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.24.1 | Room 342, 340, 339, 338, 344, 337, 336, 334 - LTHW Heating | The radiators are in good working order and should be for the next few years, however an allowance should be made for maintenance over the next few years. Replace individual units as necessary. | GB | 3 | 7200 | 0 |  |  | 3600 |  | 3600 | 0 | 0 | 0 | 0 | 0 | 0
m |  | Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.24.2 | Room 338 - HWS | The point of use hot water heater is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 2 | 600 | 0 | 600 |  |  |  |  | 0 | 600 | 0 | 0 | 0 | 0
m | 3.24.3 | Room 341 - HWS | The point of use hot water heater is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 2 | 600 | 0 | 600 |  |  |  |  | 0 | 600 | 0 | 0 | 0 | 0
m |  | Broadlands Cottage Original Part EKAH-HA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.25.6 | Plant room - Boiler | The boiler is generally in good condition and should be serviceable for the next few years, however nearing the end of its plant operational life expectancy. Replace individual units as necessary. Allowance made for an annual expenditure. | GA | 3 | 2000 | 0 |  | 1000 |  | 1000 |  | 0 | 0 | 1000 | 0 | 1000 | 0
m | 3.25.7 | Plant room - Gas Solenoid Valve/Panic button | There is no gas solenoid valve & panic button, requires upgrade/improvement. | GG | 1 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m |  | 1st Floor - Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.25.8 | Cupboard - HWS cylinder | The HWS immersion cylinder is in good working order and should be for the next several years, however the insulation cover requires repair. | GD | 2 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m | 3.25.9 | Cupboard - HWS pipework | The pipework is in good order however the insulation requires upgrade/improvement. | GD | 2 | 300 | 300 | [5 empty] | 300 | 0 | 0 | 0 | 0 | 0
m |  | 1st Floor - Air Conditioning |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.25.10 | IT room - Air Conditioning | The AC unit is not working and requires further investigation and repair. | GF | 1 | 400 | 400 | [5 empty] | 400 | 0 | 0 | 0 | 0 | 0
m |  | Humanities Block Original Part EKAH-KA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m |  | Ventilation |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.26.1 | Room 014, 015, 013 - Ventilation | The extract fan is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GE | 2 | 400 | 0 | 400 |  |  |  |  | 0 | 400 | 0 | 0 | 0 | 0
m |  | Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.26.2 | Room 001 - LTHW Heating | Fan convectors are old fittings, currently noisy in operation, will require further investigation or repair. however nearing the end of its plant operational life expectancy. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 2 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.26.3 | Room 014, 015, 013 - LTHW Heating | The radiators are in good working order and should be for the next few years, however an allowance should be made for maintenance over the next few years. | GB | 3 | 200 | 0 | 200 |  |  |  |  | 0 | 200 | 0 | 0 | 0 | 0
m | 3.26.4 | Room 003 - LTHW Heating | Fan convectors are old fittings, currently noisy in operation, will require further investigation or repair. however nearing the end of its plant operational life expectancy. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 2 | 7200 | 0 |  |  | 3600 |  | 3600 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.26.5 | Room 004 - LTHW Heating | Fan convectors are old fittings, currently noisy in operation, will require further investigation or repair. however nearing the end of its plant operational life expectancy. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 2 | 1000 | 0 |  |  | 500 |  | 500 | 0 | 0 | 0 | 500 | 0 | 500
m | 3.26.6 | Room 016 - LTHW Heating | The radiators are in good working order and should be for the next few years, however an allowance should be made for maintenance over the next few years. | GB | 3 | 200 | 0 | 200 |  |  |  |  | 0 | 200 | 0 | 0 | 0 | 0
m | 3.26.7 | Room 008 - LTHW Heating | Fan convectors are old fittings and nearing the end of its plant operational life expectancy. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 2 | 1000 | 0 |  | 500 |  | 500 |  | 0 | 0 | 500 | 0 | 500 | 0
m | 3.26.8 | Room 012, 010, 009 - LTHW Heating | The radiators are in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 2 | 1600 | 0 |  |  | 800 |  | 800 | 0 | 0 | 0 | 800 | 0 | 800
m | 3.26.9 | Plant room - Boiler | Boilers are generally in operating condition, however nearing the end of there expected operational plant life expectancy. Replace units as necessary. Allowance made far an annual expenditure. | GA | 2 | 5000 | 0 |  |  | 2500 |  | 2500 | 0 | 0 | 0 | 0 | 0 | 0
m |  | Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.26.13 | Room 014, 015, 013 - Hot Water Services | The point of use hot water heater is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 2 | 600 | 0 | 600 |  |  |  |  | 0 | 600 | 0 | 0 | 0 | 0
m | 3.26.14 | Room 007 - Hot Water Services | The point of use hot water heater is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 2 | 600 | 0 | 600 |  |  |  |  | 0 | 600 | 0 | 0 | 0 | 0
m | 3.26.15 | Room 011 - Hot Water Services | The point of use hot water heater is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 2 | 600 | 0 | 600 |  |  |  |  | 0 | 600 | 0 | 0 | 0 | 0
m |  | 1st Floor - Heating |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.26.17 | Room 354, 352, 351, 349, 348 - LTHW Heating | The radiators are in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 2 | 2400 | 0 |  |  | 1200 |  | 1200 | 0 | 0 | 0 | 1200 | 0 | 1200
m | 3.26.18 | Room 350 - LTHW Heating | The radiators are in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GB | 2 | 2400 | 0 |  |  | 1200 |  | 1200 | 0 | 0 | 0 | 1200 | 0 | 1200
m |  | 1st Floor - Domestic Water |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.26.19 | Room 350 - Hot Water Services | The unit is in operating order but will required replacement in a few years as it nears the end of its expected operational life. Replace individual units as necessary. Allowance made for an annual expenditure. | GD | 2 | 1200 | 0 |  | 600 |  | 600 |  | 0 | 0 | 600 | 0 | 600 | 0
m |  | Single Austin Hall T4 Porta Cabin |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.4.9 | Small Power/ Data Outlets | Replace surface mounted PVC socket/data outlets and FCU. | HB | 3 | 1000 | 0 |  |  | 500 |  | 500 | 0 | 0 | 0 | 500 | 0 | 500
m | 3.4.11 | Data points | Replace surface mounted PVC data sockets | HF | 3 | 500 | 0 |  |  | 250 |  | 250 | 0 | 0 | 0 | 250 | 0 | 250
m |  | CA1 & CA2 Elliott Music Block A&B Porta Cabin |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.5.6 | Lighting | Lighting to entrance lobby showing signs of deterioration. | HC | 3 | 300 | 0 |  |  | 150 |  | 150 | 0 | 0 | 0 | 150 | 0 | 150
m |  | Library Original Part EKAH/CA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.6.7 | Lighting | Replace lighting. Showing signs of ageing effecting light quality. | HC | 3 | 8000 | 0 |  | 4000 |  | 4000 |  | 0 | 0 | 0 | 0 | 0 | 0
m |  | C.D.T Original Part EKAH/EA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.8.7 | Lighting | Mix of newer and older fittings. Replace older fittings in office and classroom (linear type fittings) Yellowing diffusers. | HC | 3 | 5400 | 0 |  | 2700 |  | 2700 |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.8.9 | External Lighting | Yellowing diffusers. | HC | 3 | 1000 | 0 |  | 500 |  | 500 |  | 0 | 0 | 500 | 0 | 500 | 0
m | 3.8.11 | Switch gear | Isolators showing signs of ageing. | HA | 3 | 4000 | 0 |  | 2000 |  | 2000 |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.8.12 | DB boards | Replace DB boards, past useful life. Showing signs of ageing and deterioration. | HA | 4 | 16000 | 0 |  | 8000 |  | 8000 |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.8.13 | White PVC surface mounted conduit and mini trunking. | Replace existing and install extra trunking to area needed e.g. office | HB | 3 | 500 | 0 | 500 |  |  |  |  | 0 | 500 | 0 | 0 | 0 | 0
m |  | CA3, CA4, CA5 Elliott Art Block A,B,C Porta Cabin |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.9.1 | Switchgear | Replace switch panel, incoming switch isolator and other isolators. Repair and make weather proof housing/shed enclosure. | HA | 4 | 13000 | 0 |  |  | 6500 |  | 6500 | 0 | 0 | 0 | 0 | 0 | 0
m | 3.9.2 | Switchgear Trunking System/ General tidying | Replace galv. Steel trunking. Showing signs of rust through damp areas/leaks in housing. | HB | 3 | 500 | 0 |  |  | 250 |  | 250 | 0 | 0 | 0 | 250 | 0 | 250
m | 3.9.7 | Lighting | Lighting to entrance lobby showing signs of deterioration. | HC | 3 | 300 | 0 |  |  | 150 |  | 150 | 0 | 0 | 0 | 150 | 0 | 150
m |  | English Block Original Part EKAH/IA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.10.7 | Lighting | Lighting past useful life. Diffusers yellowing and dirty. | HC | 3 | 16000 | 0 |  | 8000 |  | 8000 |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.10.9 | External Lighting | Lighting past useful life. Diffusers yellowing and dirty. | HC | 3 | 750 | 0 | 750 |  |  |  |  | 0 | 750 | 0 | 0 | 0 | 0
m | 3.10.10 | Small Power/ Data Outlets | Replace and rewire | HB | 3 | 2000 | 0 |  |  | 1000 |  | 1000 | 0 | 0 | 0 | 1000 | 0 | 1000
m | 3.10.11 | White PVC surface mounted conduit and mini trunking. | Conduit in places missing lid and/or becoming loose (off wall/ceiling). | HB | 3 | 500 | 0 | 500 |  |  |  |  | 0 | 500 | 0 | 0 | 0 | 0
m | 3.10.12 | Data points | Replace and rewire as part of works in 3.10.10 | HF | 3 | 1400 | 0 |  |  | 700 |  | 700 | 0 | 0 | 0 | 700 | 0 | 700
m |  | Broadlands Cottage Original Part EKAH-HA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.11.7 | Lighting | Surface mounted fluorescent batten luminaire c/w prismatic diffusers need replacing. Discolouration/dirty diffuser effecting quality of light from luminaire. | HC | 3 | 300 | 0 |  |  | 150 |  | 150 | 0 | 0 | 0 | 150 | 0 | 150
m | 3.11.17 | Lighting | Surface mounted fluorescent batten luminaires c/w prismatic diffusers need replacing. Discolouration/dirty diffuser effecting quality of light from luminaire. | HC | 3 | 1200 | 0 |  |  | 600 |  | 600 | 0 | 0 | 0 | 600 | 0 | 600
m |  | Humanities Block Original Part EKAH-KA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.12.7 | Lighting | Replace fluorescent tubes that have blown within back stage area. | HC | 3 | 100 | 0 |  |  | 50 |  | 50 | 0 | 0 | 0 | 50 | 0 | 50
m | 3.12.16 | Lighting | Replace lamps to circular bulkheads in corridor 354/354a | HC | 3 | 200 | 0 |  |  | 100 |  | 100 | 0 | 0 | 0 | 100 | 0 | 100
m |  | Block B Main Teaching EKAH/BA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.1 | Incoming Switchgear | Replace switchgear - Still serviceable but has reached the end of its recommended life expectancy as defined by CIBSE guide lines | HA | 3 | 10000 | 10000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.2 |  | Verify if installation has ben inspected and tested in line with BS recommendations, if not carry out full compliance test. | HL | 2 | 1500 | 1500 | [5 empty] | 1500 | 0 | 0 | 0 | 0 | 0
m | 3.1.3 | Fire Alarm Installation. | Replace - Still serviceable but has reached the end of its recommended life expectancy as defined by CIBSE guide lines | HD | 3 | 25000 | 0 | 25000 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.4 | Security | Replace - Still serviceable but has reached the end of its recommended life expectancy as defined by CIBSE guide lines | HE | 3 | 30000 | 0 |  | 15000 |  | 15000 |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.5 | Local Distribution boards | Replace - Still serviceable but has reached the end of its recommended life expectancy as defined by CIBSE guide lines | HA | 3 | 3500 | 3500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.6 | Distribution cabling | Replace - Still serviceable but has reached the end of its recommended life expectancy as defined by CIBSE guide lines | HA | 3 | 6000 | 6000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.7 | Lighting - Gym area main corridor - Ref 38, 26, 27 | Gym Main Corridor. Damage to various luminaire diffusers | HC | 2 | 750 | 750 | [5 empty] | 750 | 0 | 0 | 0 | 0 | 0
m | 3.1.8 | Toilets male and female pupils + Disabled - ref 20 and 23 + 17 | 2 no. luminaires within the male toilet not operational at time of survey. - investigate fault and repair / replace lamps. | HC | 2 | 250 | 250 | [5 empty] | 250 | 0 | 0 | 0 | 0 | 0
m | 3.1.9 | Canteen - ref 1 | 4 no. fitting not operation during site survey, investigate fault and replace / repair as required. Various diffusers discoloured and dirty in diffuser - clean | HC | 2 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.1.10 | Room 10 | Some discolouration to the diffusers. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines | HC | 3 | 250 | 250 | [5 empty] | 250 | 0 | 0 | 0 | 0 | 0
m | 3.1.11 | Corridors - ref 11, 66, 65,61,46 | Some discolouration to the diffusers. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines | HC | 3 | 750 | 750 | [5 empty] | 750 | 0 | 0 | 0 | 0 | 0
m | 3.1.12 | Locker area - ref 63 | One of the luminaires was not operational at the time of the survey. Investigate fault, and repair / replace as required | HC | 2 | 150 | 150 | [5 empty] | 150 | 0 | 0 | 0 | 0 | 0
m | 3.1.13 | Caretakers store / room ref 384 | Part of the installation is switched via the wall mounted switch, and part by a ceiling mounted pull cord. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines | HC | 3 | 250 | 250 | [5 empty] | 250 | 0 | 0 | 0 | 0 | 0
m | 3.1.14 | Classrooms ref 48, 54, 57 & 59 | Signs of aging with discolouration of the diffusers. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - consider replacement. | HC | 3 | 3200 | 3200 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.15 | Prep room - 55, 56 & 58 | 2 no. luminaires not operation at time of survey. Signs of aging with discolouration of the diffusers. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - consider replacement. | HC | 2 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.1.16 | Gym area main corridor - Ref 26 | Existing corridor door hold open devices not operational. | HD | 2 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.1.17 | Gym office - ref 34 | Test existing distribution boards and local electrical installation with Gym area. | HL | 2 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.1.18 | IT classrooms - ref 21, 18, 15 | Due to the nature of the spaces i.e. IT rooms consideration should be given to the installation of automatic smoke/heat detection - possible higher fire risk in these area comported to standard classroom. | HD | 2 | 750 | 750 | [5 empty] | 750 | 0 | 0 | 0 | 0 | 0
m | 3.1.19 | Main Hall / stage area - ref 5 and 6 | Remove redundant switches, Local DB coming to the end of its recommended serviceable life expectance, as defined under CIBSE guide lines - consider replacement cost included under 3.1.9 | HA | 3 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.1.20 | Corridors - ref 11, 66, 65,61,46 | Small power Installation and door hold opens reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines | HB | 3 | 1500 | 0 | 1500 |  |  |  |  | 0 | 1500 | 0 | 0 | 0 | 0
m | 3.1.21 | Classrooms ref 48, 54, 57 & 59 | Small power Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines | HB | 3 | 1600 | 1600 | [5 empty] | 1600 | 0 | 0 | 0 | 0 | 0
m | 3.1.22 | Main containment for field wiring through the main block | Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines. | HA | 3 | 10000 | 10000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.23 | Lighting - Stairs - ref 84 | No emergency provisions to staircase - emergency lighting should be provided. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HH | 2 | 300 | 300 | [5 empty] | 300 | 0 | 0 | 0 | 0 | 0
m | 3.1.24 | Lighting - Male toilet to stairs half landing | Some discolouration to the diffusers. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HC | 3 | 100 | 100 | [5 empty] | 100 | 0 | 0 | 0 | 0 | 0
m | 3.1.25 | Lighting - Science Classrooms 78, 82, 83, 88 | Generally diffusers show signs of discolouration. Room 78, some of the diffusers have been replaced. Room 88, 4 no. fitting not operational. Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HC | 2 | 3200 | 0 | 3200 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.26 | Lighting - Classroom - ref 96 | Diffusers are discoloured and build up of fly's in diffuser. 1 No. fitting not working at time of survey - investigate fault and repair / replace. However the installation is reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HC | 3 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
m | 3.1.27 | Lighting - Female toilets | Consideration to the installation of prismatic diffuser to existing fitting or full replacement, as the installation is reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines | HC | 3 | 150 | 150 | [5 empty] | 150 | 0 | 0 | 0 | 0 | 0
m | 3.1.28 | Lighting - Classroom 88a | Generally diffusers show signs of discolouration. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HC | 3 | 1600 | 0 |  | 800 |  | 800 |  | 0 | 0 | 800 | 0 | 800 | 0
m | 3.1.29 | Lighting - Staff Room - ref 93 | Visual signs of a water leak - 2 no. fitting not operational at the time of the survey - Investigate and repair / replace as required. | HC | 2 | 350 | 350 | [5 empty] | 350 | 0 | 0 | 0 | 0 | 0
m | 3.1.30 | Lighting - Corridor / stairs - ref 103 | No indication of emergency lighting - emergency lighting to be provided. Generally diffusers show signs of discolouration. Installation reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HH | 2 | 900 | 0 |  | 450 |  | 450 |  | 0 | 0 | 450 | 0 | 450 | 0
m | 3.1.31 | Small power - Science Classrooms 78, 82, 83, 88 | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 2400 | 0 | 2400 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.1.32 | Small power - Prep rooms 80, & 87 | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 800 | 0 | 800 |  |  |  |  | 0 | 800 | 0 | 0 | 0 | 0
m | 3.1.33 | Small power - Classroom - ref 96 | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 400 | 0 | 400 |  |  |  |  | 0 | 400 | 0 | 0 | 0 | 0
m | 3.1.34 | Small power - Classroom 88a | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 2400 | 0 |  | 1200 |  | 1200 |  | 0 | 0 | 1200 | 0 | 1200 | 0
m | 3.1.35 | Small power - Staff Room - ref 93 | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 1600 | 0 |  | 800 |  | 800 |  | 0 | 0 | 800 | 0 | 800 | 0
m |  | B Block Sports Hall EKAH/BB |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.2.1 | Switchgear | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HA | 3 | 3500 | 0 | 3500 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.2.2 | Lighting | End of Life - Consideration should be give to the installation of protective wire girds around luminaires to protect from future damage | HC | 3 | 1500 | 0 | 1500 |  |  |  |  | 0 | 1500 | 0 | 0 | 0 | 0
m | 3.2.3 | Emergency Lighting | Consideration to provide additional emergency lighting within the general service luminaires should be given when replacing the existing light fittings. | HH | 3 | 1000 | 0 | 1000 |  |  |  |  | 0 | 1000 | 0 | 0 | 0 | 0
m | 3.2.4 | Small Power/ Data Outlets | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 1000 | 0 | 1000 |  |  |  |  | 0 | 1000 | 0 | 0 | 0 | 0
m |  | Home Economics Original Part EKAH/FA |  |  |  | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.3.1 | Fire Alarm Installation. | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HD | 3 | 2500 | 0 | 2500 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
m | 3.3.2 | Security | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HE | 3 | 3500 | 3500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
m | 3.3.3 | Small power - Classroom - ref 121 | Relocate socket outlets and lighting switch's away from sink locations. | HB | 2 | 500 | 500 | [5 empty] | 500 | 0 | 0 | 0 | 0 | 0
m | 3.3.4 | Small power - Classroom - ref 124 - hand dryers | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 250 | 250 | [5 empty] | 250 | 0 | 0 | 0 | 0 | 0
m | 3.3.5 | Lighting - Classroom - ref 136 | One of the luminaires was not operational at the time of the survey within room 136 - Investigate the fault and repair / renew. Signs of discolouration to diffusers. | HC | 3 | 100 | 100 | [5 empty] | 100 | 0 | 0 | 0 | 0 | 0
m | 3.3.6 | Lighting - Store room 128 | Luminaire not operational at the time of the survey - Investigate fault and repair / renew | HC | 3 | 100 | 100 | [5 empty] | 100 | 0 | 0 | 0 | 0 | 0
m | 3.3.7 | Lighting - Classroom - ref 127 & 126 | 2 No. luminaires not operational at the time of the survey within room 127 - Investigate fault and repair / renew | HC | 3 | 200 | 200 | [5 empty] | 200 | 0 | 0 | 0 | 0 | 0
m | 3.3.8 | Lighting - Stairs | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HC | 3 | 300 | 300 | [5 empty] | 300 | 0 | 0 | 0 | 0 | 0
m | 3.3.9 | Lighting - Toilets | Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HC | 3 | 300 | 300 | [5 empty] | 300 | 0 | 0 | 0 | 0 | 0
m | 3.3.10 | Small power Toilets First floor | Power to hand dryer - Newlec Installations reaching the end of its recommended serviceable life expectancy, as defined by CIBSE guide lines - Consider replacement | HB | 3 | 250 | 250 | [5 empty] | 250 | 0 | 0 | 0 | 0 | 0

## EFA Property
|  |  | EFA survey data | [6 empty] | External Grounds | Roof Works | External Walls | Windows and Doors | Internal Works | Mechanical & Electrical | Other
DFE | School | School Type | Date received | Condition rating C or D | Priority rating 1 or 2 | Element | Category | CCP rating
|  |  |  | C | 2 | External walls windows and doors, Walls and external finishes, Timber cladding, Main block | e | eC2 | C1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  |  |  | C | 2 | Fixed Furniture, Teaching Science Technology, Generally, Main block | i | iC2 | C2 | 1 | 4 | 5 | 5 | 7 | 4 | 0
|  |  |  | C | 2 | Redecorations, Extrnal walls, Painted, Main Block | e | eC2 | D1 | 0 | 1 | 0 | 1 | 0 | 0 | 0
|  |  |  | C | 2 | Redecorations, External windows, doors etc, Metal Painted, Main block | w | wC2 | D2 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  |  |  | C | 2 | Redecorations, Intrnal walls, Painted, Main Block | i | iC2 | D3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | C | 2 | Roofs, Coverings and insulations, Flat roof- Flexible sheet, Single ply,Main Block | r | rC2
|  |  |  | C | 2 | Roofs, Coverings and nsulation, Pitched roof, Flexible schettte, single ply, Main block | r | rC2
|  |  |  | C | 2 | Roofs, Drainage, Flat roof, Cast ironRoofs, Drainage, Pitched roof, cast iron, Main Block | r | rC2
|  |  |  | C | 2 | Electrical services, Power, Generally, Food Tech | m | mC2
|  |  |  | C | 2 | Intrnal walls and doors, Walls and partitions-structure, Glazed screen, Food Tech | i | iC2
|  |  |  | C | 2 | Mechanical Services, Heating distribution emitters and controls, Generally, food Tech | m | mC2
|  |  |  | D | 1 | Roofs, Coverings and insulation, Flat roof, Flexible sheet, single ply or built up, Food Tech | r | rD1
|  |  |  | C | 2 | Redecorations, External windows, doors etc, Timber, Mobile | w | wC2
|  |  |  | C | 2 | External walls windows and doors, Windows and dorrs, Metal, CDT block | e | eC2
|  |  |  | C | 2 | Floors and Stairs, Floors screed and finish, Carpet, CDT Block | i | iC2
|  |  |  | C | 2 | Redecoration, External walls, Painted, CDT Block, | e | eC2
|  |  |  | C | 1 | Redecoration, External windows doors etc, Timber, CDT block | w | wC1
|  |  |  | C | 2 | Roofs, Drainage, Flat roof-Plastic, CDT block | w | wC2
|  |  |  | D | 2 | Electrical services, Power, Generally, Broadlands House | r | rD2
|  |  |  | C | 2 | Electrical services, Alarms, Generally, Broadlandshouse | m | mC2
|  |  |  | C | 2 | External Walls windows and doors, Windows and doors, Timber, Broadlands House | e | eC2
|  |  |  | C | 2 | External walls windows and doors, Windows and doors, Metal | w | wC2
|  |  |  | C | 2 | Floors and Stairs, Floors screed and finish, Carpet | i | iC2
|  |  |  | D | 1 | Redecoration, External windows, doors etc, Timber, Broadlands House | w | wD1
|  |  |  | C | 2 | Redecoration, Internal walls, Painted, Broadlands house | i | iC2
|  |  |  | C | 2 | Redecoration, Internal WIndows, doors etc, Generally, Broadlands house | i | iC2
|  |  |  | C | 2 | Roofs, Drainage, Pitched roof, Cast iron, Broadlands House | r | rC2
|  |  |  | C | 2 | Mechanical services, Heat source equipment generally, G Block | m | mC2
|  |  |  | C | 2 | Redecorations, External windws doors etc, Timber, G Block | w | wC2
|  |  |  | C | 2 | External areas, Other walls, fences and barriers, Generally | g | gC2

## Suitability and Compliance
Space |  | BB103 suggested sizes
|  |  |  | Suitability Data |  |  |  | Compliance Comparison |  |  |  |  | 90
Basic Teaching Spaces |  | No. of spaces | Total m2 | Actual no. of spaces | Plan ref | Space |  | Total area | Shortfall | Surplus | 2015 | Date of last assessment
| General Classroom | - |  | 16 | 28,48,49,54,57,59,94,108,110,121A,123,136,334,336,337,339,340 | General | 970.46 | 1234.333
| Art Classroom | - |  | 1 | 169 | Art | 83.84 | 83.84 |  |  | 3 | No. Temp Buildings on Site
| Science Laboratory | - |  | 5 | 78,82,83,88,92 | Science | 398.4 | 398.4 |  |  | 1 | No. of Classrooms in Temporary Buildings
| Music Classroom | - |  | 1 | 284 | Music | 48.47 | 48.47
| Drama Classroom | - |  |  |  | Drama |  | 0
| IT Classroom | - |  | 4 | 127129135137 | IT room | 201.29 | 201.29
| DT Classroom | - |  | 3 | 124,160A,160B,161 | Tech | 309.85 | 309.85
| Total | - | 1473.75 |  |  |  |  | 2276.183 | 0 | 802.433 | 154.4% | of the recommended basic teaching space required
Halls and Studios |  | - | 742.5 |  | 1,5,6,30,42 | Gym, Gym, Hall, Dining area, Stage area | 835.94 | 835.94 | 0 | 93.44 | 112.6% | of the recommended hall size
Storage |  | - | 308.75 |  | 2,3,7,16,19,22,24,29,31,37A,43,50,55,56,58,75,80,86,87,91,100,101,104,109,111,113,115,122,128,133,140,160,162,164,165,166,168,168A,220,221,223,224,225,227,229,231,232,233,234,234A,235,236,237,242,244,245,248,252,262,264,279,329,331,335,341,372,384,384A,UN35,UN74,UN77,UN85,UN87,UN94 |  | 1044.249 | 1044.249 | 0 | 735.499 | 338.2% | of the recommended storage space required
Staff and admin |  | - | 261.25 |  | 9,9A,15,17,17A,27A,34,34A,93,105,106,114,121,126,134,139,139A,141,163,217,218,251,253,254,255,277,338,343,UN41,UN88,UN91,UN93 | Offices, meeting rooms, reprographics | 686.65 | 686.65 | 0 | 425.4 | 262.8% | of the recommended staff and admin space required
Learning resource area |  | - | 190 |  | 18,21,25,112,215,342,UN76,UN79,UN81,UN82,UN84,UN92 |  | 292.79 | 292.79 | 0 | 102.79 | 154.1% | of the recommended learning resource areas
Supplementary area |  | - | 0 |  |  |  |  | 0 | 0 | 0 | - | of the recommended supplementary areas
Non net areas |  | - | 1199.3 |  | 4,4A,8,10,10A,11,13,13A,14,14A,26,26A,26B,27,27B,27D,32,33,33A,33B,33C,33D,33E,35,36,37,37B,37C,38,38A,38B,38C,41,41A,46,47,53,61,63,65,66,66A,69,69A,69B,69C,70,71,72,74,77,79,81,84,88A,89,90,95,96,97,98,99,102,103,107,116,118,118A,118B,120,124A,124B,125,130,131,138,142,216,216A,219,222,226,228,230,238,239,241,243,246,249,250,256,257,258,259,260,260A,261,263,330,344,344A,344B,344C,383,UN1,UN2,UN3,UN4,UN5,UN6,UN7,UN8,UN9,UN10,UN11,UN12,UN13,UN14,UN15,UN16,UN25,UN26,UN27,UN28,UN29,UN30,UN31,UN32,UN33,UN34,UN36,UN37,UN38,UN39,UN42,UN43,UN45,UN46,UN47,UN50,UN55,UN57,UN58,UN59,UN62,UN63,UN64,UN65,UN66,UN67,UN68,UN69,UN71,UN73,UN75,UN78,UN80,UN86,UN90 | Corridor, stairs, landing, changing rooms, staff wc's, disabled wc's, boiler room, server room, electrics room, | 1331.5 | 1439.96 | 0 | 240.66 | 120.1% | of the recommended non net area
| Pupils toilets | 24 |  | 37 | 20,23,44,44A,45,62,64,119,132,UN72,UN89 | Toilets (male and female pupil wc's) | 108.46 |  |  |  | 154.2% | % of recommended pupil toilets
Total Net area |  |  | 2976.25 |  |  |  |  | 5135.812
Total Non-Net area |  |  | 1199.3 |  |  |  |  | 1439.96
Gross (total build) area |  |  | 4175.55 |  |  |  |  | 6575.772 |  |  | 157.5% | of the recommended Gross area
Net Area Range |  |  | 2775 - 3080
Mid Range |  |  | 2927.5
Total Site Area Range |  |  | 31357.5 - 39375
Mid Range |  |  | 35366.25

## Occupancy
Sufficiency Data
Planned Admission Number | Post 16 Planned Admission Number | Current Capacity | Maximum PAN | Capacity based on max PAN
90 | - | 450 | 111.6 | 558
NOR Spring Census
| 2008 / 2009 | 2009 / 2010 | 2010 / 2011 | 2011 / 2012 | 2012 / 2013 | 2013 / 2014
NOR Jan (11-16) | 864 | 761 | 689 | 605 | 551 | 478
NOR Jan (Post 16) | 0 | 0 | 0 | 0 | 0 | 0
Total NOR Jan | 864 | 761 | 689 | 605 | 551 | 478
Capacity (11-16) | 1050 | 900 | 750 | 750 | 750 | 750
Capacity (Post 16) | 0 | 0 | 0 | 0 | 0 | 0
Total capacity | 1050 | 900 | 750 | 750 | 750 | 750
Number of surplus places (11-16) | 186 | 139 | 61 | 145 | 199 | 272
Number of surplus places (Post 16) | 0 | 0 | 0 | 0 | 0 | 0
Total number of surplus places | 186 | 139 | 61 | 145 | 199 | 272
% of surplus places (11-16) | 17.7143 | 15.4444 | 8.1333 | 19.3333 | 26.5333 | 36.2667
% of surplus places (Post 16) | 0 | 0 | 0 | 0 | 0 | 0
Total % of surplus places | 17.7143 | 15.4444 | 8.1333 | 19.3333 | 26.5333 | 36.2667
Current Numbers on Roll (from Autumn Census)
Year group | 7 | 8 | 9 | 10 | 11 | 12 | 13 | Total
Number | 70 | 72 | 102 | 89 | 108 | 0 | 0 | 441

## School stats
Current Ofsted | Year
Good | 2011-10-12
2014 KS4 Performance Tables last update : (29 Jan 2015)
Cohort information
Number of pupils at the end of KS4 | 113
Key Stage 2 APS of cohort | 27.7
| Number in cohort | Percentage of cohort
Low attainers | 13 | 13%
Middle attainers | 58 | 56%
High attainers | 32 | 31%
Pupils for whom English is not their first language | 10 | 9%
Pupils with statements or supported at school action plus | 11 | 10%
Year on year comparisons
Percentage achieving 5+ A*-C GCSEs (or equivalent) including English and maths GCSEs | 2011 | 2012 | 2013 | 2014
School | 58% | 35% | 46% | 50%
LA | 57.5% | 56.5% | 56.1% | 58.7%
England - All Schools | 59% | 59.4% | 59.2% | 53.4%
KS4 exam results
| All pupils | Low attainers | Middle attainers | High attainers
Percentage achieving 5 A*-C GCSEs (or equivalents) including English and maths GCSEs | 50% | 0% | 43% | 94%
Percentage achieving A*-C in English and maths GCSEs | 51% | 0% | 45% | 94%
Percentage of pupils achieving the EBacc | 19% | 0% | 7% | 53%
Percentage of pupils achieving 5+ A*-C grade GCSEs (or equivalent) | 63%
Percentage of pupils achieving 5+ A*-G grade GCSEs (or equivalent) | 96%
% of pupils achieving any qualifications | 100%
Number of KS4 pupils with entries in all EBacc subject areas | 33 | 0 | 11 | 21
Percentage of pupils with entries in all EBacc subject areas | 29% | 0% | 19% | 66%
KS4 pupil progress
| All pupils | Low attainers | Middle attainers | High attainers
Percentage of pupils making expected progress in English | 67% | 54% | 60% | 88%
Percentage of pupils making expected progress in maths | 63% | 23% | 59% | 88%
Best 8 value added | 998 | 1015.3 | 997.1 | 992.6
Lower confidence limit | 983.8 | 975.5 | 978.2 | 967.3
Upper confidence limit | 1012.1 | 1055.1 | 1015.9 | 1018
Percentage of pupils included in VA measure | 91%
KS4 Average Point Scores
| All pupils | Low attainers | Middle attainers | High attainers
Total average (capped) point score per pupil | 312.5 | 215 | 302.6 | 381.3
Average grade per qualification |  | E+ | C- | B
KS4 Exam entries
| All pupils | Low attainers | Middle attainers | High attainers
Average entries per pupil - all qualifications | 9.6 | 7.2 | 9.5 | 11
Disadvantaged Pupils
| Disadvantaged pupils | Other pupils
Number of Pupils | 16 | 97
Percentage of Pupils | 14% | 86%
Percentage achieving grades A*-C in English and maths GCSEs | 31% | 55%
Percentage achieving 5+ A*-C GCSEs (or equivalent) including English and maths GCSEs | 31% | 54%
Percentage of pupils making expected progress in English | 56% | 69%
Percentage of pupils making expected progress in maths | 38% | 68%
Best 8 VA measure | 1004.4 | 996.9
Best 8 VA lower 95% confidence limit for disadvantaged pupils | 967.3 | 981.6
Best 8 VA upper 95% confidence limit for disadvantaged pupils | 1041.4 | 1012.2
Average entries per pupil - all qualifications | 8.9 | 9.7
Average point score per pupil (best 8) - all qualifications | 284.9 | 317.1
For the purposes of the table Disadvantaged pupils are considered as those eligible for free school meals and children
looked after (ie, In the care of the Local Authority for at least 6 months)
Pupil Absence last update : (11 Dec 2013)
| School | England - national (secondary state-funded)
Overall absence: percentage | 6% | 5.8%
Persistent absence: around 15% + | 6.7% | 6.5%
Please note - this year the Department will publish full year 2013/14 absence data in the performance tables in March 2015 rather than just the autumn and spring term data in December as in previous years, and we will continue to do so in future years. This is because the full year data provides the most robust indication of school absence rates.
School level information for the 2013/14 autumn and spring term only is available in our Statistical First Release here
2013-14 Finance last update : (29 Jan 2015)
Contextual information
Number of pupils (FTE) | 478
Percentage of pupils eligible for Free School Meals (FSM) | 7.5%
Free school meals eligibility band | LOW
Spend per pupil data as £ per pupil (in brackets percentage of total income or expenditure)
| School | LA Median | Non-London LAs Median | National Median
Grant funding | 5907 (97%) | 5205 | 5267 | 5720
Self generated income | 205 (3%) | 143 | 146 | 141
Total income | 6112 | 5312 | 5467 | 5904
Teaching staff | 3783 (61%) | 3079 | 3010 | 3159
Supply Staff | 23 (0%) | 77 | 96 | 114
Education support staff | 578 (9%) | 475 | 556 | 606
Learning resources (not ICT equipment) | 238 (4%) | 232 | 220 | 242
ICT learning resources | 54 (1%) | 67 | 77 | 82
Bought in professional services - curriculum | 14 (0%) | 33 | 58 | 66
Back office (incl. Staff costs) | 603 (10%) | 431 | 480 | 531
Catering (incl. Staff costs) | 23 (0%) | 25 | 42 | 62
Premises (incl. Staff costs) | 402 (6%) | 363 | 349 | 381
Other staff costs | 54 (1%) | 87 | 85 | 95
Energy | 127 (2%) | 84 | 98 | 103
Other expenditure | 298 (5%) | 257 | 209 | 219
Total expenditure | 6196 | 5223 | 5385 | 5856
Spend per pupil data as £ per pupil : Comparisons over time
| 2010-11 | 2011-12 | 2012-13 | 2013-14
Teaching staff and Education support staff expenditure | 3964 | 4110 | 4063 | 4360
Supply staff | 139 | 43 | 17 | 23
Back office (incl. Staff costs) | 556 | 524 | 530 | 603
Energy | 87 | 97 | 107 | 127
Total expenditure | 5978 | 5989 | 5823 | 6196
School Workforce last update : (29 Jan 2015)
This data is based upon the November 2013 School Workforce Census
| School | England - national (secondary state-funded)
Headcount of all teachers in a school | 38 | 227957
Headcount of all teaching assistants in a school | 12 | 68901
Headcount of all support (exc. auxiliary) staff in a school | 14 | 89346
Full-time equivalent number of all teachers in a school | 36.9 | 211533
Full-time equivalent number of all teaching assistants in a school | 8.1 | 53876.9
Full-time equivalent number of all support (exc. auxiliary) staff in a school | 12.5 | 74423.5
Ratio of pupils to teachers in a school | 13 | 15
Average gross salary of all teachers in a school | 38792 | 38521
Ofsted Inspection last update : (31 Jan 2015)
Inspection date | 2011-10-12
Inspection outcome | 2
Web link | Link to Ofsted inspection report
Education Destination Measure for 2011/12 cohort last update : (29 Jan 2015)
| School | England - national (secondary state-funded)
Number of pupils | 150 | 561800
Total in a sustained education destination | 81% | 88%
Further Education College | 30% | 34%
Independent School | 0% | SP
Other Further Education Provider | 7% | 3%
School Sixth Form | 2% | 37%
Sixth Form College | 42% | 12%
Specialist post-16 institution | 0% | SP
Pupil Referral Unit or Other Alternative Provision | 0% | SP
Special School | 0% | 1%
Apprenticeships | 8% | 4%
UK Higher Education Institution | 0% | SP
Education combination | 0% | SP
Education destination not sustained | 9% | 7%
Activity not captured in data | 10% | 4%

## Parental Preference
Popularity Data | [10 empty] | Children at School From School Catchment
Parental First Preference Applications | [11 empty] | 2010 | 2011 | 2012 | 2013 | 2014 |  | Catchment vs Nearest School | Catchment | Nearest
Year | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 |  |  |  |  | NOR | 761 | 689 | 605 | 551 | 478 |  | NOR | 441 | 441
PAN | 210 | 180 | 150 | 150 | 150 | 150 |  |  |  |  | Number | 516 | 451 | 409 | 391 | 347 |  | Total in area | 1065 | 604
No. | 115.5 | 86.4 | 96 | 103.05 | 87 | 73 |  |  |  |  | % | 67.8055 | 65.4572 | 67.6033 | 70.9619 | 72.5941 |  | Number at School from area | 334 | 176
% | 55 | 48 | 64 | 68.7 | 58 | 48.6667 | [11 empty] | % at School | 75.737 | 39.9093
[11 empty] | Total number in Catchment | [6 empty] | % of area going to School | 31.3615 | 29.1391
[12 empty] | 2010 | 2011 | 2012 | 2013 | 2014
[11 empty] | Number | 1076 | 1029 | 1001 | 1059 | 1063
[11 empty] | % | 100 | 100 | 100 | 100 | 100
Where children at School are coming from (from Spring Census 2014)
DCSF No | School |  | Queen Elizabeth | Whitecross | Aylestone | The Minster | Weobley | The John Masefield | The John Kyrle | Bishops | Hereford Academy | Out of County | Grand Total
4015 | Aylestone | Number | 3 | 51 | 347 | 8 | 4 | 6 | 2 | 10 | 45 | 2 | 478
4015 | Aylestone | % | 0.62762 | 10.6695 | 72.5941 | 1.6736 | 0.83682 | 1.2552 | 0.41841 | 2.0921 | 9.4142 | 0.41841 | 100
Where school children in the Schools Catchment area are going to (from Spring Census 2014)
DCSF | School |  | Robert Owen | Queen Elizabeth | Whitecross | Aylestone | Kingstone | Lady Hawkins | The Minster | Fairfield | Weobley | The John Masefield | The John Kyrle | Bishops | St Marys RC | Hereford Academy | Grand Total
4015 | Aylestone | Number | 6 | 9 | 126 | 347 | 6 | 2 | 1 | 7 | 12 | 5 | 2 | 320 | 200 | 20 | 1063
4015 | Aylestone | % | 0.56444 | 0.84666 | 11.8532 | 32.6435 | 0.56444 | 0.18815 | 0.094073 | 0.65851 | 1.1289 | 0.47037 | 0.18815 | 30.1035 | 18.8147 | 1.8815 | 100

## Disability access
Physical Accessibility Rating | 1
Information from https://www.herefordshire.gov.uk/education-and-learning/schools/directory
Ratings and descriptions
Rating | Details | Description
3 | Fully accessible | Will meet the needs of all disabled pupils: all standards met including all curriculum areas accessible (may be achieved by timetabling); Has a full hygiene room and special educational needs or therapy room for pupils who need more assistance with personal care (including hoisting) and regular physio or other treatment
2 | Mainly accessible | Will meet the needs of most disabled pupils: all standards met including all curriculum areas accessible (may be achieved by timetabling) but no hygiene room
1 | Partly accessible | Some standards met but some areas not accessible
0 | Inaccessible | No level access into building and/or no disabled toilet
Summary of physical accessibility standards
Level access into building(s): Main and pupil entrance(s) level, with ramps and hand rails as required
Level access to all curriculum and social areas (not necessarily entire building/site): including assembly hall, canteen (may be achieved by sensitive organisation and timetabling)
Access to upper floors: if required - lift(s) as alternative to steps or stairs
Toilet facilities: small disabled toilet(s) as specified by building regulations - suitable for most disabled pupils. A small number of pupils will require enhanced facilities (hygiene room) to provide greater assistance, including hoisting.
Medical, therapy or SEN room: multi-purpose or flexible use - usually required in addition to a hygiene room, for regular physio and other physical programmes
Emergency evacuation: routes should be level and unobstructed. Evacuation must be documented (using Personal Emergency Evacuation Plans - PEEPs) and practised regularly